SECTION 26 09 13 94 10

ELECTRICAL POWER MONITORING AND CONTROL

- GENERAL

  - SCOPE

    - This section defines low voltage Power Metering for use in AC systems, rated 600 V or less.

  - RELATED DOCUMENTS

    - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

    - [Related Sections (where applicable) include the following:

      - Section 16441 – Switchboards

      - Section 16443 – Motor Control Centers]

  - SUBMITTALS

    - Submit shop drawings and product data for approval and final documentation in the quantities listed according to the Conditions of the Contract.  Customer name, customer location and customer order number shall identify all transmittals.

    - [Final Documents: Record documentation to include wiring diagrams, instruction and installation manuals [and certified test reports].]

  - RELATED STANDARDS

    - Meet the following recognized standards for application in hardened environments

      - Power meter must meet all international standards for Safety and Construction applicable to this type of device:

        - ANSI C12.20, "Electricity Meters - 0.2 and 0.5 Accuracy Classes – Part 5.5.4 Accuracy tests.”

        - ANSI / ISA – 61010-1, “Safety Requirements for Electrical Equipment for Measurement, Control, and Laboratory Use – Part 1:  General Requirements.”

        - ANSI / ISA – 61010-2-030, “Safety Requirements for Electrical Equipment for Measurement, Control, and Laboratory Use - Part 2-030: Particular requirements for testing and measuring circuits.”

        - CAN/CSA C22.2 No. 61010-1, “Safety Requirements for Electrical Equipment for Measurement, Control, and Laboratory Use - Part 1: General Requirements.”

        - CAN/CSA C22.2 No. 61010-2-030, “Safety Requirements for Electrical Equipment for Electrical Equipment for Measurement, Control, and Laboratory Use - Part 2-030: Particular requirements for testing and measuring circuits.”

      - Power meter must meet the following international standard for Electromagnetic Immunity applicable to this type of device:

        - EN 50160, “Voltage Characteristics of Electricity Supplied by Public Distribution Systems.”

        - EN 55011, “Limits and Methods of Measurement of Radio Interference Characteristics of Industrial, Scientific, and Medical Equipment.”

        - EN 55022, “Information Technology Equipment - Radio Disturbance Characteristics - Limits and Methods of Measurement.

        - EN 50470-1, EN 50470-3  Electricity Metering Equipment (a.c.) Part 1 and Part 3

      - Federal Communications Commission (FCC):

        - Title 47 CFR Part 15, Subpart B, "Radio Frequency Devices."

      - Institute of Electrical and Electronics Engineers, Inc. (IEEE):

        - ANSI/IEEE C37.90.1, "Surge Withstanding Capability (SWC) Tests for Protective Relays and Relay Systems."

        - IEEE 802.3 – 2012, “Standard for Ethernet.”

        - IEEE 1815 - 2012, “Standard for Electrical Power Systems Communications – Distributed Network Protocol (DNP3).”

      - Industry Canada (IC) Standards, Interference Causing Equipment Standard (ICES):

        - ICES 003, “Information Technology Equipment (ITE) - Limits and Methods of Measurement.”

      - International Electrotechnical Commission (IEC):

        - CISPR 22, “Information Technology Equipment – Radio Disturbance Characteristics – Limits and Methods of Measurements.”  	ICES 003, “Information Technology Equipment (ITE) - Limits and Methods of Measurement.”

        - IEC 61000-3-2, “Part 3: Limits - Section 2: Limits for Harmonic Current Emissions (Equipment Input Current ≤16 Amperes per Phase).”

        - IEC 61000-3-3, “Part 3: Limits - Section 3: Limitation of Voltage Fluctuations and flicker in Low-Voltage Supply Systems for Equipment with Rated Current ≤16 Amperes.”

        - IEC 61000-4-2, “Electromagnetic compatibility (EMC) - Part 2-4: Environment - Compatibility levels in industrial plants for low-frequency conducted disturbances.”

        - IEC 61000-4-3, “Electromagnetic compatibility (EMC) - Part 4-3: Testing and measurement techniques - Radiated, radio-frequency, electromagnetic field immunity test.”

        - IEC 61000-4-4, “Electromagnetic compatibility (EMC) - Part 4-4: Testing and measurement techniques - Electrical fast transient/burst immunity test.”

        - IEC 61000-4-5, “Electromagnetic compatibility (EMC) - Part 4-5: Testing and measurement techniques - Surge immunity test.”

        - IEC 61000-4-6, “Electromagnetic compatibility (EMC) - Part 4-6: Testing and measurement techniques - Immunity to conducted disturbances, induced by radio-frequency fields.”

        - IEC 61000-4-7, “Electromagnetic Compatibility (EMC) - Part 4-7: Testing and Measurement Techniques; General Guide on Harmonics and Interharmonics Measurements and Instrumentation, for Power Supply Systems and Equipment Connected Thereto.”

        - IEC 61000-4-8, “Electromagnetic compatibility (EMC) - Part 4-8: Testing and measurement techniques - Power frequency magnetic field immunity test.”

        - IEC 61000-4-11 “Electromagnetic compatibility (EMC) - Part 4-11: Testing and measurement techniques - Voltage dips, short interruptions and voltage variations immunity tests."

        - IEC 61000 4 12, “Electromagnetic compatibility (EMC) - Part 4-12: Testing and measurement techniques - Ring wave immunity test.”

        - ii.	IEC 61000-4-19, “Electromagnetic compatibility (EMC) – Part 4-19: Testing and Measurement Techniques – Test for Immunity to Conducted, Differential Mode Disturbances and Signaling in the Frequency Range 2 kHz to 150kHz at A.C. Power Ports.”

        - IEC 61000-4-30, “Electromagnetic Compatibility (EMC) - Part 4-30: Testing and Measurement Techniques; Power Quality Measurements Methods.”

        - IEC 61010-1, “Safety Requirements for Electrical Equipment for Measurement, Control and Laboratory Use - Part 1: General Requirements.”

        - IEC 61010-030-12, “Safety Requirements for Electrical Equipment for Measurement, Control, and Laboratory Use - Part 2-030: Particular requirements for testing and measuring circuits”

        - IEC 61557-12, “Electrical safety in low voltage distributions systems up to 1,000 V a.c. and 1,500 V d.c. – Equipment for testing, measuring or monitoring of protective measures – Part 12: Performance measuring and monitoring devices (PMD).”

        - IEC 61850 Edition 1, “Communication networks and systems for power utility automation.”

        - IEC 62052-11, “Electricity Metering Equipment (AC) - General Requirements, Tests and Test Conditions - Part 11: Metering Equipment.”

        - IEC 62052-31, “Electricity Metering Equipment (AC) – General Requirements, Tests and Test Conditions – Safety Requirements.”

        - IEC 62053-22, “Electricity Metering Equipment (AC) - Particular Requirements - Part 22: Static Meters for Active Energy (Classes 0,2 S and 0,5 S).”

        - IEC 62053-23, “Electricity Metering Equipment (AC) - Particular Requirements - Part 23: Static Meters for Reactive Energy (Classes 2 and 3).”

        - IEC 62053-24, “Electrical metering equipment (AC) – Particular requirements – Part 24:  Static meters for reactive energy (classes 0.5 and 1).”

        - IEC 62586, “Power quality measurement in power supply systems.”

      - Underwriters Laboratories, Inc. (UL):

        - UL. 61010-1, “Safety Requirements for Electrical Equipment for Measurement, Control, and Laboratory Use - Part 1: General Requirements.”

        - UL 61010-2-030, “Safety Requirements for Electrical Equipment for Electrical Equipment for Measurement, Control, and Laboratory Use - Part 2-030: Particular requirements for testing and measuring circuits.”

  - QUALITY ASSURANCE

    - Manufacturer Qualifications: Manufacturer of this equipment shall have a minimum of 5 years experience producing similar electrical equipment.

      - Comply with requirements of latest revisions of applicable industry standards.

  - DELIVERY, STORAGE AND HANDLING

    - Store and handle in strict compliance with manufacturer’s instructions and recommendations.  Protect from potential damage from weather and construction operations.  If the meters are installed in equipment, store the equipment so condensation will not form on or in it.  If necessary, apply temporary heat where required to obtain suitable service conditions.

- PRODUCTS

  - MANUFACTURERS

    - The low voltage Power Meter shall be type 9410 by Siemens Industry Inc., or pre-approved equal.  Approved manufacturers are as follows:

      - SIEMENS - ACCESS

      - [     ]

  - General Provisions

    - All setup parameters required by the Power Meter shall be stored in nonvolatile memory and retained in the event of a control power interruption.

    - The Power Meter may be applied in [4-wire wye] [3-wire wye] [3-wire delta] [direct delta] [single phase] systems.

    - A one-piece and remote display (Tran) design shall be available for the meter.

    - The Power Meter shall be fully supported by Power Meter Software including advanced features like waveform capture, on-board logging and alarms.

  - COMPONENTS

    - Current/Voltage Inputs

      - The Power Meter shall have no less than 3 voltage inputs and 4 current inputs.

      - The Power Meter in its standard configuration shall be able to accept 600VLL/347VLN (UL) 400 VLN/690 VLL (IEC) without using potential transformers.

      - The Power Meter shall be able to withstand 3300 volts AC RMS for 2 seconds without damaging the device.

      - The Power Meter shall support nominal current ratings of 1 amperes or 5 amperes and an over current of 500 amperes for 1 second

    - Control Power

      - The power meter shall be able to accept a wide range of control power inputs the range of 90 V AC to 415 V AC +/- 10% (45 to 65 Hz), 90 V AC to 120 V AC +/- 10% (400 Hz) or 120 V DC to 300 V DC +/- 10% without need for a control power transformer.

      - The Power meter shall have the ability to sustain operation through a control power outage of 10 cycles, minimum, and ensure any events resulting in a control power outage will be captured.

    - Mechanical

      - The Power meter shall be available in multiple form factors for panel mounting with an integrated display, and for DIN rail mounting without a display or with a remotely mounted display.

      - The panel mount meter with integrated display shall mount in a ¼ DIN, 92 x 92 mm (3.622” x 3.622”), cut-out without the need for tools.

      - The DIN rail mount meter, without a display, shall mount on a TS35 (35mm x 7.5mm) DIN rail without the need for tools.

      - The remotely mounted display shall support mounting in a ¼ DIN, 92 x 92 mm (3.622” x 3.622”), cutout, and support mounting in a 30.5 mm round hole (M30 punch).

      - The panel mount meter and the remotely mounted display shall meet UL/NEMA Type 12 and IP54 installation criteria when properly installed.

      - The power meter unit shall have removable connectors for voltage inputs, control power, communications, inputs, and outputs.

    - Environmental

      - The power meter shall have an operating temperature rating of -25 to 70 ºC (-13 to 158 ºF).

      - The power meter shall be installable in environments up to 3000 meters (9843 feet), relative humidity of 5% to 95% non-condensing (to a maximum dewpoint of 37 ºC), pollution degree 2.

      - The power meter shall be fully compliant with RoHS European directive ensuring the product does not include any of the 6 substances stated in the directive.

      - The power meter shall be fully compliant with the REACH European regulation ensuring the product does not include any of the identified Substances of Very High Concern (SVHC).

      - The power meter manufacturer shall provide, on request, a Product Environmental Profile (PEP) that provides a list of material, a recycling rate and a calculation of eleven environmental impacts such as raw material, energy consumption, carbon footprint and damage to the ozone layer that spans the entire product life cycle, from manufacture to end of working life.

      - The power meter manufacturer shall provide, on request, an End of Life Instruction guide (EoLI) providing clear instructions for recycling and disposal of the Power meter at the end of its working life.

    - Measured Values

      - The Power Meter shall provide the following, true RMS metered quantities for voltage:

        - Voltage L–L Per-Phase

        - Voltage L-L 3-Phase Avg

        - Voltage L–N Per-Phase

        - Voltage 3-Phase Avg

        - Voltage % unbalanced

        - Voltage L-L Min/Max

        - Voltage L-N Min/Max

        - Voltage L-L, Unbalanced Min/Max

        - Voltage L-N, Unbalanced Min/Max

      - The Power Meter shall provide the following true RMS metered quantities for current:

        - Current Per-Phase

        - Current, Neutral (measured)

        - Current 3-Phase Avg

        - Current % Unbalanced

        - Current Min/Max

      - The Power Meter shall provide the following true RMS metered quantities for power:

        - Real Power (Per-Phase, 3-Phase Total)

        - Reactive Power (Per-Phase, 3-Phase Total)

        - Apparent Power (Per-Phase, 3-Phase Total)

        - Power Factor – True (Per-Phase, 3-Phase Total)

        - Power Factor – Displacement (Per-Phase, 3-Phase Total)

        - True Power Factor Total – Min/Max

        - Displacement Power Factor Total – Min/Max

        - Real Power Factor Total – Min/Max

        - Reactive Power Total – Min/Max

        - Apparent Power Total – Min/Max

        - THD – Voltage, Current (3-Phase, Per-Phase, Neutral)

        - Fundamental Voltage, Magnitude and Angle (Per-Phase)

        - Fundamental Current, Magnitude and Angle (Per-Phase)

        - Fundamental Real Power (Per-Phase, 3-Phase)

        - Fundamental reactive Power (Per-Phase)

        - Phase Rotation Unbalance (Current and Voltage)

        - Harmonic Magnitudes & Angles for Current and Voltage (Per Phase) up to the 63rd Harmonic.

      - The Power Meter shall provide the following true RMS metered quantities for energy:

        - Accumulated Energy (Real kWh, Reactive kVARh, Apparent kVAh) (Signed/Absolute)

        - Incremental Energy (Real kWh, Reactive kVARh, Apparent kVAh) (Signed/Absolute)

        - Conditional Energy (Real kWh, Reactive kVARh, Apparent kVAh) (Signed/Absolute)

        - Reactive Energy by Quadrant

      - The power meter shall be capable of deriving values for any combination of measured or calculated parameter, using the following arithmetic, trigonometric, and logic functions:

        - Arithmetic functions; division, multiplication, addition, subtraction, power, absolute value, square root, average, maximum, minimum, RMS, sum, sum-of-squares, unary minus, integer ceiling, integer floor, modulus, exponent, PI.

        - Trigonometric functions; COS, SIN, TAN, ARCCOS, ARCSIN, ARCTAN, LN, LOG10.

        - Logic functions; =, =>, <=, <>, <, >, AND, NAND, OR, NOR and XOR.

        - Temperature conversion functions; C to F, F to C.

    - Demand

      - The Power meter shall be able to provide last completed interval demand, predicted demand, peak demand with date and time, and coincident demand values on multiple demand channels.

      - The power meter shall be able to perform multiple accepted demand calculation methods, including, but not limited to, block, rolling block, and thermal demand with user-programmable demand period lengths.

      - The power meter shall support the synchronization of the demand interval using a digital input, a command via communications, or internal clock.

    - Accuracy

      - The Power Meter shall meet ANSI C12.20 0.2 as per IEC 61557-12.

      - The Power Meter shall meet IEC 62053-22 class 0.2s (real energy)

      - The Power Meter shall meet IEC 62053-24 class 0.5s (reactive energy)

      - The Power Meter shall provide four-quadrant metering.

    - Sampling

      - The Power Meter shall perform zero-blind metering and sample at a minimum of 256 samples per cycle, simultaneously on all voltage and current channels in the meter.

      - The Power Meter shall be able to perform sag/swell detection of voltage disturbances on a half-cycle basis, providing the duration of the disturbance, the minimum, maximum, and average value of the voltage for each phase during the disturbance. Disturbances less than one cycle in duration can be detected.

    - Memory

      - The power meter shall have at least 512MB of non-volatile memory for configuration settings, log data, events, waveform captures, web pages and documents.

      - The Power meter shall store critical internal and revenue data upon sudden power loss.

      - The Power meter shall retain all data and configuration in non-volatile memory for 15 years without control power.

      - The Power meter shall provide a real time clock (RTC) with battery backup that will provide ride-through of at least 7 years without control power once installed, 10 years in storage.

      - The Power meter shall have a field installable battery for real time clock ride-through that can be installed without need to remove the instrument from the installation.

      - The Power meter shall have a time-stamped event log with the following features:

        - Shall support at least 500 events.

        - The number of records in the log shall be programmable.

        - Each event shall be recorded with the date and time of the event, the cause and effect of the event, and the priority of the event.

        - Events relating to setpoint activity, relay operation, and self-diagnostics shall be recorded in the event log.

        - Time stamps shall have a resolution of 1 millisecond

        - Time stamps can be synchronized to within +/- 1 millisecond between devices through the use of GPS (Global Positioning Satellites) serial input or (IRIG-B digital input) or SNTP server with +/-1 second and NTP with 10-100ms.

        - Minimum event recording response time shall be 1/2 cycle (8.3 ms 60 hertz, 10 ms 50 hertz) for high speed events and 1 second for other events.

        - The priority of set point events shall be programmable.

      - The Power Meter shall be able to log any parameter in the meter, including, but not limited to, minimum/maximum and waveforms.

      - The Power meter shall be capable of supporting a minimum of 50 independent data logs that support the following configuration options:

        - Recording method of Fill and Hold or First In First Out (FIFO).

        - Selection of up to 16 parameters per log.

        - Log data on an event or based on internal clock.

        - Ability to automatically fill gaps in data logs with a value of zero (0) or leave blank.

    - Alarming

      - The Power meter shall have the ability to support a minimum of 65 setpoint driven alarms evaluated once per second or once every ½ cycle, user configurable

      - The Power meter shall have the ability to support disturbance alarms for detecting voltage and current dips and current dips and swells on all monitored phases

      - The Power meter shall be able to generate an E-mail on an alarm condition.

      - The Power meter shall have millisecond time stamp resolution on alarm entries.

      - The Power meter shall be able to adjust alarm setpoints based on the alarm quantity (alarm setpoint learning).

        - The user shall be able to enable the Power meter to learn the characteristics of normal operation of metered values and selected alarm setpoints based on this data

        - The quantities to be learned shall be user selectable, including, but not limited to, standard speed alarms, high speed alarms, and disturbance alarms.

        - The user shall be able to configure this feature using one of two modes:

          - Manual: Once the learning is completed, the recommended values shall be stored for review and manual installation.

          - Automatic: Once the learning is completed, the recommended values shall be automatically installed and operational.

        - The learning period shall be user configurable from 1 to 365 days to ensure system stability prior to determining the recommended setpoints.

      - The power meter shall support consecutive high speed alarm conditions which shall trigger on a cycle-by-cycle basis with no delay time between events (i.e., no need for a rearming delay time between events).

      - The power meter shall be able to operate relays on alarm conditions.

      - The power meter shall be able to initiate data log captures on alarm conditions.

      - The power meter shall be able to control digital output relays using pulse mode or latch mode operation, for control and alarm purposes.

      - The power meter shall be able to combine any logical combination of any number of available setpoint conditions to control any internal or external function or event.

    - Communications

      - The Power Meter shall be capable of the following communications methods:

        - Ethernet (Dual-port, single network) 10/100 Base –TX on both ports

        - Ethernet Switch 10/100 Base –TX on either port

        - Ethernet Switch with RSTP ( Rapid Spanning Tree Protocol) 10/100 Base TX on both

        - Serial  - RS-485.

      - The Power Meter shall support multiple concurrent Ethernet communication protocols over an Ethernet network at any one time:

        - IEC61850

        - DNP3.0 TCP/IP

        - Modbus TCP/IP

        - Modbus TCP/IP Mastering of Ethernet devices

        - ION TCP/IP

        - Ethernet serial line gateway

        - FTP (file transfer)

        - HTTP (web interface)

        - NTP/SNTP (time synchronization)

        - SMTP (Email)

        - SNMP ( simple management with traps)

        - MV-90 compatibility

      - The Power meter shall support any one of the following serial communications protocols on any one serial port at any one time:

        - Modbus

          - Modbus RTU

          - Modbus mastering of serial RS-485 slaves

        - DNP 3.0

        - ION

        - MV-90 compatibility

      - The Power meter shall be able to support at least 32 concurrent Modbus TCP/IP connections.

      - The Power meter shall be able to support at least 32 Modbus RTU (serial) devices into the RS-485 port and act as a Modbus TCP gateway or Modbus master unit.

      - The power meter shall support up to eight (8) simultaneous supervisory connections through the TCP Ethernet port.

      - The Power meter shall have a Modbus TCP/IP gateway to provide a network connection to Modbus serial devices connected to a serial port on the instrument.

      - The Power meter shall have the ability to read from and write to Modbus devices connected to a serial port on the instrument and on a common local area Ethernet network.

      - The Power meter shall serve web pages with the following capabilities to:

        - Provide real-time and historical data views in both tabular and graphical formats

        - Provide a histogram of harmonic data through the 63rd harmonic.

        - Provide an ITIC (CBEMA) and a SEMI E10 summary of voltage disturbances.

        - Provide a NEMA motor derating curve.

        - Provide a phasor diagram representation of the electrical connections to the meter.

        - Provide a summary of EN 50160 power quality data along with a pass / fail analysis

        - Provide a graphical trend for voltage, average current, frequency and power demand along with a forecast of the next 4 points

        - Support the ability to provide technical documents and drawings in PDF format

        - Support user defined web pages containing data from the host meter as well as data from Modbus devices connected to a serial port on the instrument and on a common local area Ethernet network.

      - The Power meters shall have two (2) Ethernet ports that support the following functions:

        - Automatically E-mail alarm notifications or scheduled system status updates. E-mail messages sent by the Power meters shall be able to be received like any ordinary E-mail message.

        - Ability to push historical logs through the Ethernet communication port to a remote server based on a user defined schedule or an event.

        - Built in web pages in the Power meters shall enable access to real-time values and basic power quality information using a current standard web browser. Basic configuration of the Power meters shall also be able to be performed through the browser.

      - The Power meters shall automatically provide E-mail notifications for alarms and system status updates based on user configuration.

      - The Power meter shall have the ability to push historical logs through the Ethernet communication port to a remote server based on a user defined schedule or an event.

      - The Power meter shall provide an IEC 61850 compliant communications interface with the following features:

        - Four (4) concurrent client connections

        - File based setup via FTP.

        - Network time sync via NTP

        - Configurable reports, including, but not limited to, selectable dataset member and configurable dead band values.

        - Support four (4) buffered reports and twenty (20) unbuffered reports (one (1) buffered and five (5) unbuffered per client).

        - Map up to 16 analog and/or 16 digital calculated values for reporting in IEC 61850.

        - Fault capture data for three-phase voltage and current in COMTRADE format, including, but not limited to, the following:

          - Up to 225 COMTRADE fault capture files.

          - The files shall be downloadable via standard FTP client.

          - The device shall support client notification through IEC 61850 to signal when new fault captures have been created and are available (RDRE logical node).

        - The following logical nodes shall be supported in addition to LLNO and LPHD (mandatory):

          - MHAI; harmonics.

          - MMTR; metering.

          - MMXU; measurement.

          - MSQI; sequence and imbalance.

          - MSTA; metering statistics.

          - GGIO; the ability to view data from and control all I/O points in the meter.

          - RDRE; disturbance recorder function.

      - The power meter shall have the ability to announce its presence on a local network segment using Device Profile Web Services (DPWS) over IPv6 local addressing without user interaction.  The instrument shall be viewable in a Microsoft™ Windows™ Windows Explorer window view of network devices as a link that will provide access to the instrument’s web interface.

    - I/O Options

      - The Power meter shall be capable of having 27 digital inputs capable of one (1) millisecond timing resolution.

      - The Power meter shall be capable of receiving unmodulated IRIG-B time synchronization protocol through integrated digital inputs to ensure system wide time accuracy.

      - The Power meter shall have a Form A digital output that shall support pulse output operation for kWh total, kWh imported, kWh exported, kVARh total, kVARh imported, kVARh exported, and kVAh values.

      - The Power meter shall have an optical test output that is compliant with IEC 62052-11.

      - The Power meter shall be capable of supporting up to four (4) field installable option modules to expand digital and analog I/O capabilities without need for additional control power sources

      - The Power meter shall be capable of having up to eight (8) Form C relays which shall be isolated for up to 3200 volts AC (2 seconds), with reinforced isolation rated for 300 V.  Overvoltage Category II.  The relays shall support maximum current of eight (8) amperes continuous for 250VAC or five (5) amperes continuous for 24 volts DC for 20,000 cycles (resistive load)

      - The Power meter shall be capable of having up to sixteen (16) Analog inputs which shall be isolated and support inputs of four (4) to twenty (20) milliamps or zero (0) to twenty-four (24 volts) volts DC.

      - The Power Meter shall be capable of having up to sixteen (16) Analog inputs which shall be isolated and support inputs of four (4) to twenty (20) milliamps or zero (0) to twenty-four (24 volts) volts DC.  The Power meter shall be capable of providing consumption and rate of usage information with user defined units of measure from pulse inputs to support metering of utilities such as water, air, gas, electricity and steam (WAGES).

    - Display

      - The Power meter shall have two (2) graphical color display options: an integral display and a remote mounted display.

        - The panel mounted Power meter shall have an integral 320 x 240 pixel backlit color graphical LCD display, TFT, 2.8 inches (71 mm) by 2.1 inches (53 mm).

        - The DIN rail mounted Power Meter shall have a remotely mounted 320 x 240 pixel backlit color graphical LCD display, TFT, 2.8 inches (71 mm) by 2.1 inches (53 mm).

        - The remote display shall be fully powered by and capable of communicating with the Power Meter.

        - The remotely mounted display shall be able to be located up 100 meters (330 feet) from the Power Meter and be powered through a standard Cat5/5e unshielded twisted pair cable.

        - The displays shall be suitable for NEMA / UL type 12 (IP 54) enclosures.

        - The remotely mounted display shall perform and function in the same manner as the integrated display.

      - The Power Meter shall be capable of presenting all real-time parameters on the instrument’s display.

      - The Power Meter shall have a user-programmable custom display that shall be capable of displaying up to six (6) quantities on a single screen.

      - The Power Meter shall be capable of displaying advanced graphical representations of metering information, including, but not limited to, harmonic histograms, phasor diagrams, and bar graphs.

      - The Power Meter shall be able to display measurements in either IEC or IEEE formats.

      - The Power Meter display shall support multiple languages, including, but not limited to, English, French, Spanish, German, Italian, Portuguese, Russian, and Chinese.

      - The Power Meter shall be able to present the following display screens:

        - Numeric: Display one (1) parameter , one (1) parameter with timestamp, two (2) parameters, three (3) parameters, three (3) parameters with timestamp, or four (4) parameters at a time.

        - Event Log: Display recent events written to the PM instrument’s event log, including, but not limited to, diagnostic events.

        - Nameplate: Display information in a tabular format (default nameplates shall show Owner, and meter details).

        - Bar: Display up to three (3) real time numeric parameters along with their upper and lower extremes.

        - Histogram: Display harmonics content in histogram format, including, but not limited to, 2nd to 63rd harmonic, THD (total, even, odd); ability to select and display magnitude and angle for individual harmonics

      - Phasor:  Display color coded current and voltage phase information in a phasor diagram format, including tabular display of magnitudes and angles.

      - Inputs and Outputs:  Display digital input and output status, and analog input and output values.

      - Alarm:  Display a listing of active and historical alarms and events.

    - Power Quality

      - Without the use of separate software, the Power Meter shall be able to measure power quality statistically in accordance with IEC 61000-4-30, Class S.  The Power Meter shall perform EN50160 power quality evaluations.

      - The Power Meter shall be certified by a third party as compliant with IEC 61000-4-30 Class S, Edition.

      - The Power Meter shall be certified by a third party as compliant with IEC 62586.

      - Without using separate software, the Power Meter shall determine statistical indicators of power quality parameters that shall include, but shall not be limited to dips and swells, harmonics, and frequency, in accordance with the EN 50160 standard.

      - Without the use of separate software, the Power Meter shall make available the statistical indicators of power quality provided by EN50160 on the instrument’s display, or via communications protocols such as ION, Modbus RTU, Modbus TCP/IP, or via web pages.

      - The Power Meter shall be capable of monitoring the value of any statistical indicator of power quality (present, predicted, average, or otherwise manipulated value) with an absolute or relative setpoint. When such setpoint is exceeded, an alert shall be issued via E-mail or pager, or control shall be enabled via a local interface to mitigation equipment or control systems through relays and analog or digital outputs.

      - The Power Meter shall support symmetrical components.

    - Waveform Capture

      - The Power Meter shall be able to perform 256 samples per cycle waveform recording.

      - The Power Meter shall have twenty-one (21) programmable oscillographic waveform recorders. Each waveform recorder shall have the following features:

        - Able to record a digitized representation of any phase voltage or current signal with no dead time between such recordings, and the ability to trigger multiple such recordings in continuous succession, and at different resolutions simultaneously.

        - Enabled and triggered manually or through internal operating conditions, including, but not limited to, periodic timer or setpoint activity.

        - Half-cycle triggering shall be supported for waveform recorders.

        - The number of records (depth) of each data recorder, and the overflow conditions (stop-when-full or circular) shall be programmable.

      - The Power Meter shall be able to record continuously to capture long duration waveforms. The duration of the waveform capture shall be limited by memory alone.

      - The Power Meter shall be able to determine (with a level of confidence) whether a disturbance event occurred upstream or downstream of the meter (disturbance direction detection).

    - High-Speed Data Logging:

      - The Power Meter shall be capable of recording high-speed data captures containing one (1) cycle RMS data updated every half (1/2) cycle.

      - The Power Meter shall be able to record seconds of high-speed data per data capture.

      - The Power Meter shall be able to initiate a high-speed data capture based on a setpoint condition, user programmed logical condition, or command received via communication.

      - The Power Meter shall be capable of capturing high-speed logs concurrently with a waveform capture.

    - Advanced Features

      - The Power Meter firmware shall be field upgradeable over TCP or Serial connections.

      - Onboard meter clock shall be able to be paced by a choice of sources, including, but not limited to, GPS, Ethernet network (NTP/SNTP), power line, or internal clock.

      - The Power Meter shall have multi-level security which shall support customized access for up to 16 users.

      - The Power Meter shall have revenue security capabilities, including, but not limited to, the following:

        - Password protected, no hardware lock, or

        - Password protected and hardware locked, or

        - The following data shall be protected from alteration when locked:

          - kWh and kVARh (import, export, net, and total).

          - kVAh (total).

          - kW, kVAR, kVA demand ( block and sliding window).

          - kWh, kVARh, kVAh pulse outputs.

      - The Power Meter shall have selective conformal coating of its internal circuitry for increased isolation and to increase robustness of installations exposed to high degrees of humidity.

      - The Power Meter shall have provisions for creating periodic or non-periodic schedules for up to two (2) years. These schedules shall be used to perform the following functions:

        - Time of use (TOU).

        - Demand control.

        - Load scheduling.

        - Logging.

        - Periodic resetting.

      - The Power Meter shall provide a physical lock switch that will preserve all meteorological configuration values to ensure accurate and consistent energy metering.

      - The Power Meter shall provide the ability to secure its meteorological lock switch as well as all voltage and current inputs with tamper detectable wire seals.

      - The Power Meter shall have multiple tariffs and time-of-use (TOU) functionality to store and monitor up to twenty (20) years of seasonal rate schedules. The TOU feature shall allow four (4) seasons, four (4) day types (each one capable of at least eight (8) switch times, with a resolution of one (1) minute). The TOU feature shall support four (4) rate tariffs, and at least twelve (12) holidays per year, and shall allow periodic self-read capability.

      - The Power Meter shall support trending and forecasting of real-time data values with visualization via device generated web pages.

- EXECUTION

  - INSTALLATION

    - The meter shall be installed at the factory by a manufacturer’s trained employee.

    - Additional connections to metering systems, where applicable, shall be done in the field by [the manufacturer’s start-up service group] [the installing contractor].

  - ADJUSTING AND CLEANING

    - The meters shall be adjusted so that accurate readings appear on the front of the meter and that the readings are within the meters accuracy range.

    - Clean exposed surfaces using manufacturer recommended materials and methods.

  - TESTING

    - Perform factory and installation tests in accordance with applicable NEC, NEMA and UL requirements.

  - WARRANTY

    - Equipment manufacturer warrants that all goods supplied are free of non-conformities in workmanship and materials for one year from date of initial operation, but not more than eighteen months from date of shipment.

  - [STARTUP SERVICES]

    - [Engage a factory-authorized service representative to perform startup service.]

    - [Train Owner's maintenance personnel on procedures and schedules for energizing and de-energizing, troubleshooting, servicing and maintaining equipment and schedules.]

    - [Verify that the [meter is] [meters are] installed and connected according to the Contract Documents.]

    - [Verify that electrical control wiring installation complies with manufacturer's submittal by means of point-to-point continuity testing.  Verify that wiring installation complies with requirements in Division 16 Sections.]

    - [Complete installation and startup checks according to manufacturer's written instructions.]

END OF SECTION