# SECTION 26 24 13.02

# MULTI-METERING SWITCHBOARDS

- GENERAL

  - SCOPE

    - The contractor shall provide and install [service entrance] [distribution] switchboards as herein specified and shown on related electrical drawings

  - RELATED DOCUMENTS

    - All of the Contract Documents, including General and Supplementary Conditions and Division 1 General Requirements, apply to the work of this Section.

    - [Related sections include the following:

      - [Section 26 28 16 – Molded Case Breakers]

      - [Section 26 43 13 – Surge Protection Devices For Low-Voltage Electrical Power Circuits]

      - [Section 26 09 13 – Electrical Power Monitoring and Control]

      - [Section 26 24 13 – Switchboards]

      - [Section 26 24 16 – Panelboards]

      - [Section 26 22 13 – Low-Voltage Distribution Transformers]

  - SUBMITTALS

    - Product Data: Submit manufacturer's printed product data.

    - Drawings: Submit shop drawings for approval.  Include components, materials, finishes, detailed plan and elevation views, required conduit rough-in openings, anchors and accessories.

  - RELATED STANDARDS

    - The switchboard shall be designed, manufactured and tested according to the latest applicable version of the following standards:

      - NEMA PB2 – Deadfront Distribution Switchboards

      - UL 891 – Deadfront Switchboards

    - [Manufacturer Seismic Qualification: The low voltage switchboard(s) shall meet and be certified to seismic requirements specified in the [IBC 2015 International Building Code] [CBC 2016 California Building Code] [ASCE American Society of Civil Engineers 7-10].

      - The low voltage switchboard(s) shall be compliant with IBC 2015 parameters:

        - Building Occupancy Category (as defined in Table 1.1 from ASCE 2010): [I] [II] [III] [IV]

        - Seismic Design Category: [A] [B] [C] [D] [E] [F]

        - Site Class: [A – Hard Rock] [B - Rock] [C – Very dense soil and soft rock] [D – Stiff soil profile] [E – Soft Soil Profile] [F – Soil vulnerable to potential failure or collapse under seismic loading] as defined in IBC 2006 Table 1613.5.2 Site Class Definitions

        - Ip – Importance Factor: [1.5 – Components must function after an earthquake for life safety purposes (Building Occupancy Code IV)] [1.25 - Buildings and structures that represent a substantial hazard to human life in the event of failure or that can cause substantial economic impact or mass disruption of day-to-day civilian life (Building Occupancy Code III)] [1.0 – Non-essential buildings.  Function not life critical. (Building Occupancy Code I and II)]

        - Ss – Mapped Spectral Accelerations for Short Periods at 0.2 seconds – 239%g

        - Sds – 5% Damped Design Spectral Response Accelerations for Short Periods at 0.2 seconds – [Floor 0, Sds=2.70g] [Floor 1, Sds=2.32g] [Floor 2, Sds=2.03g] [Floor 3, Sds=1.80g] [Floors 4-12, Sds=1.69g]

        - z/h – Height factor ratio: [___]  Note: Ratio is a calculated value equal to the floor the gear is installed on divided by 12.  A 6th floor installation is a 0.5 value.  A basement or ground floor installation is a 0.0 value.

      - Equipment shall be designed to be located in a concrete and steel, moment-resisting frame building not exceeding 12 stories in height with a minimum story height of 10 feet.]

  - QUALITY ASSURANCE

    - Manufacturer: For equipment required for the work of this section, provide product which is the responsibility of one manufacturer.

    - Performance Requirements: Provide switchboards manufactured in accordance with Article 408 of the latest National Electrical Code and applicable portions of the NEMA PB2, UL 891 and NFPA 70, the National Electrical Code.

  - DELIVERY, STORAGE AND HANDLING

    - Deliver materials and products in factory labeled packages.  Store and handle in strict compliance with manufacturer's instructions and recommendations.  Protect from damage from weather, excessive temperatures and construction operations.

- PRODUCTS

  - MANUFACTURERS

    - Provide switchboards and accessories by Siemens type SMM/MMS or pre-approved equal.  Approved manufacturers are as follows:

      - SIEMENS

      - [     ]

    - For the equipment specified herein, the manufacturer shall be ISO 9000, 9001 or 9002 certified.

    - The manufacturer of this equipment shall have produced similar electrical equipment for a minimum of ten (10) years.

    - Intent: In the following specifications, products of Siemens are used to provide a standard of quality and performance for the work of this section.

  - GENERAL REQUIREMENTS

    - Construction

      - Switchboard shall be of the modular type construction, constructed in accordance with the latest NEMA PB-2 and UL 891 standards, with the required number of vertical sections bolted together to form one metal enclosed rigid switchboard.  The sides, top and rear shall be covered with removable screw-on code gauge steel plates.  Switchboard shall include all protective devices and equipment as listed on drawings with necessary interconnections, instrumentation and control wiring.  All groups of control wires leaving the switchboard shall be provided with terminal blocks with suitable numbering strips.  Service entrance switchboards shall be suitable only for use as service equipment and be labeled in accordance with UL requirements.  System voltage, amperage and interrupting capacity shall be as indicated on the drawings.  Enclosure construction shall be [NEMA 1 indoor] [NEMA 3R outdoor].

    - Bus Requirements

      - The bus shall be [of sufficient size to limit the temperature rise to 65 degree C, based on UL tests] [750A / sq-in for aluminum] [1000A / sq-in for copper] and [shall be tapered per UL standards] [shall be fully rated the entire length of the switchboard]. The bus shall be braced and supported to withstand mechanical forces exerted during a short circuit from a power source having the available short circuit current as indicated on the drawings.  Provide a full capacity neutral where a neutral is indicated on the drawings.  The through bus on the end section shall be extended and pre-drilled to allow the addition of future sections.  Ground bus and grounding conductor lug shall be furnished.  Ground bus shall extend the entire length of the switchboard and shall be firmly secured to each vertical section. Bus material shall be [tin plated aluminum] [silver-plated copper].

    - Incoming Service [NOTE: Select Underground or Overhead service.  If Overhead, then select between cable or bus]

      - [Underground Service

        - To isolate incoming underground service conductors, an underground cable pull or auxiliary section shall be used when shown on the drawings.  This section shall be of the [non-bussed] [bussed] type and shall be sealable per local utility requirements, when required.  ]

      - [Overhead Service

        - [Cable entry: Where necessary, provide top cable pull box and provide construction that shall be sealable per local utility requirements, when required.]

        - [Busway Entry: Integrated switchboard to be fed by Siemens Sentron [______] ampere [copper] [aluminum] busway, as detailed on drawings [and other sections of this specification].  The integrated switchboard manufacturer shall be responsible for coordination, proper phasing and internal bussing to the incoming busway.]]

      - Service Section:

        - The service section shall be designed for the system parameters indicated and shall have [a metering compartment per utility requirements] [user metering as indicated] and shall have a main protective device indicated.

      - Lugs:

        - [Screw-type mechanical lugs] [Compression lugs] to terminate [aluminum] [copper] Cable shall be provided as detailed on the 0064rawings.

    - [Fire Pump Tap

      - The fire pump tap section shall be ahead of the main breaker and contain only through bus and tap lugs to feed the fire pump.]

    - [Utility Metering

      - The utility metering section shall be built in accordance with requirements and codes of the local utility.]

    - [Main Lugs Only [Select either this Main Lugs Only section or Main Protective Device section below.  Delete the section that does not apply in its entirety.]

      - The switchboard shall be main lugs only.  Switchboards used for service entrance shall be limited to six disconnects.]

    - Main Protective Device [NOTE: Select 1 of the 6 main devices from the list below]

      - [Molded Case Circuit Breaker shall be of the quick-make, quick-break, trip-free, [thermal magnetic] [solid state] type. When solid state breakers are used, the continuous current rating shall be adjustable from 20 to 100% without the need for a rating plug.  Solid state breakers shall be Siemens Sensitrip III, VL or equivalent design. Solid state breaker trip functions shall include adjustments for continuous amperage, long time pickup and delay, instantaneous [short time pickup and delay,] [ground fault pickup and delay,] [zone selective interlocking for short time and ground fault,].  Breaker ratings shall be as shown on the drawings.]

      - [Solid State, Molded Case Circuit Breaker] [Molded case circuit breaker shall be of the quick-make, quick-break, trip-free, solid state type. The solid state breakers continuous current rating shall be adjustable from 20 to 100% without the need for a rating plug.  Solid state breakers shall be Siemens Sensitrip III, VL or equivalent design. Solid state breaker trip functions shall include adjustments for continuous amperage, long time pickup and delay, instantaneous [short time pickup and delay,] [ground fault pickup and delay,] [zone selective interlocking for short time and ground fault].  Breaker ratings shall be as shown on the drawings.]

        - [The main breaker shall have a Dynamic Arc Flash Sentry.  The main breaker shall have a dual protective setting capability similar to the Siemens VL breakers ETU586 trip unit with Sm@rt DAS controller.  The main breaker will allow the installer to set two different short time and instantaneous settings into one breaker.  One set of settings will be set for standard operating mode and the second settings, with instantaneous protection shall be set for arc flash mode.] [The switchboard shall be outfitted with a 24 VDC power supply, Sm@rt DAS controller, annunciator panel with flashing light and a UPS power supply.  The arc flash mode shall be actuated by a [Siguard motion sensor set to the arc flash boundary] [keyed switch] [light curtain shall be installed behind the gear to sense open doors on the back of the panel.] [The breakers with frames rated 1200 amps or larger shall be equipped with Sm@rt Dynamic Arc Flash Sentry to comply with NEC 2014 240.87.]]

      - [Fusible Switch

        - [Fusible switch shall be of the quick-make, quick-break, trip-free type.  Switch shall be Siemens Vacu-break design or equivalent.  Switch ratings and options shall be shown on the drawings.]

        - [High contact pressure switch shall be quick-make, quick-break, trip-free type.  Switch shall be Siemens HCP type or equivalent.  Switch ratings and options shall be as shown on the drawings. [Switch shall include ground fault protection and indication.]]

      - [Bolted Pressure Switch shall be true bolted contact load break type with provisions for Class L fuses.  Switches shall have an interrupting rating of 12 times the continuous rating and capable of carrying 100% of rated current.  High pressure contact switches do not meet the intent of this requirement.  [Switch shall include ground fault protection and indication.]  ]

      - [Low Voltage Power Circuit Breaker shall be provided with a drawout frame and current rating as shown on the drawings.  It shall be [manually] [electrically] operated power circuit breaker with a solid-state trip device providing adjustments for long time pick up and delay, [short time pickup and delay,] [instantaneous,] [ground fault pickup and delay,] [and zone selective interlocking for short time and ground fault].  Breaker shall be Siemens Type WL design or equivalent.]

      - [WL Insulated Case Breaker, Fixed Mount Main]

        - Circuit breakers shall comply with the requirements of UL489.  Breakers shall be three-pole, 100% rated type or approved equal.

          - Circuit beaker element shall have spring charged/discharged indicators and circuit breaker open or closed and ready to close indicators all of which shall be visible to the operator with the compartment door closed.

          - Provide interlocks to prevent racking the circuit breaker unless the breaker is open

        - Ratings: Interrupting up to 100 kA at 480V without fuses. Short time current ratings for each circuit breaker shall be as indicated on the drawings or data tables. Circuit breakers shall be 600-volt class.

        - Operating Mechanism: Mechanically and electrically trip-free, stored-energy operating mechanism with the following features:

          - Normal Closing Speed: independent of both control and operator

          - [Electrical operator, field installable with manual charging]

          - [Operations counter]

        - Each low voltage circuit breaker shall be equipped with self-powered, microprocessor-based trip-device to sense overload and short circuit conditions.  The device shall measure true RMS current.  The tripping system shall consist of high accuracy (<1%) Rogowski coil sensors on each phase, a release mechanism and the following features:

          - Field Installable and interchangeable front mounted trip units. Trip units can be upgraded for future expansion in functionality, such as communication.

          - Functions: Long time, short time and extended instantaneous protection function shall be provided (EIP) to allow the breaker to be applied at the withstand rating of the breaker with minus 0% tolerance so that there is no instantaneous override whatsoever. This feature shall furthermore allow the circuit breaker to be applied up to the full instantaneous rating of the breaker on systems where the available fault current exceeds the breakers withstand rating. Each shall have an adjustable pick-up setting.  In addition, long time and short time bands shall each have adjustable time delay.  Short time function shall include a switchable I2t ramp and optionally I4t to improve coordination with fuses or inverse relays.

          - A software program shall be made available free of charge to support system coordination studies.  The software will allow time current curves to be generated for the chosen settings.

          - Individual LED’s shall indicate an overcurrent, short circuit or ground fault trip condition.

          - Time-current characteristics shall be field adjustable locally or optionally remotely via a bus system [ModBus] [Profibus] [Ethernet].

          - Current Adjustability shall be accomplished by use of [dial settings] [keypad] and rating plugs on trip units.  The rating plug shall be front mounted and upgradeable.  Upgrades to the rating plugs shall not require changes to the CT.

          - Pickup Points: 10 Long Time Settings.

          - [Field Installable Ground-fault protection with at least three time-delay bands and an adjustable current pickup and an I2t ramp.]  Arrange to provide protection for [three-wire] [four-wire] service.

          - [Field installable zone selective interlocking: Connections will be made between main, tie and feeder circuit breakers to ensure that the circuit breaker closest to the fault trips for short time and ground fault conditions.]

          - [Field Installable Communications and metering functions shall be provided per schedule]

          - [A LCD display shall be available to simplify settings & viewing data locally.]

          - The option to remotely switch protection settings shall be provided whenever a generator is part of the power distribution system.

          - Field installable configurable [analog], [digital] output relays shall be available to connect directly to the trip unit

          - [Waveform capture and display shall be accomplished on the trip units LCD display. ETU776 only]

        - Terminal Block Connections, shall be front mounted and utilize [Screw Type Terminals], [Ring Tongue Terminals], [Tension Spring Terminals]

        - [Control Switch: One for each electrically operated circuit breaker.]

        - [Key Interlocks: Mountings and hardware are included where future installation of key-interlock devices is indicated.]  A total of 14 different interlocking devices shall be available.

        - [Undervoltage Trip – field installable]: [Instantaneous] [Adjustable time-delay.]

        - [Shunt-Trip – field installable]

        - [Indicating Lights: To indicate circuit breaker is open or closed, for electrically operated circuit breakers.]

        - [Modular communication and relaying accessories are to be available for retrofitting by the clients chosen engineer.  It shall not be necessary for the manufacturer’s personnel to retrofit accessories.  ]

        - Accessories shall be front mounted.

        - Portable lifting yoke for drawout circuit breakers.

        - Field interchangeable accessories shall include CT’s, trip units, racking mechanism and all internal & external accessories.

        - [The main breaker shall have a Dynamic Arc Flash Sentry.  The main breaker shall have a dual protective setting capability with graphic waveform display, similar to the Siemens WL breakers ETU776 trip unit.  The main breaker will allow the installer to set two different trip curves into one breaker.  One curve will be set for standard operating mode and the second curve, with instantaneous protection shall be set for arc flash mode.   The switchboard shall be outfitted with a 24 VDC power supply, CubicleBus digital input module, annunciator panel with flashing light and a UPS power supply.  The arc flash mode shall be actuated by a [Siguard motion sensor set to the arc flash boundary] [keyed switch].  [A light curtain shall be installed behind the gear to sense open doors on the back of the panel.]]

      - [WL Insulated Case Breaker, Drawout]

        - Circuit breakers shall comply with the requirements of UL489 and UL1066.  Breakers shall be three-pole, 100% rated type or approved equal.

          - Circuit beaker element shall have connected, test and disconnected position indicators, spring charged/discharged indicators and circuit breaker open or closed and ready to close indicators all of which shall be visible to the operator with the compartment door closed.  It shall be possible to rack the circuit breaker element from the connected to the disconnected position with the compartment door closed, otherwise known as “through the door drawout”.

          - Provide interlocks to prevent racking the circuit breaker unless the breaker is open

        - Ratings: Interrupting up to 100 kA at 480V without fuses. Short time current ratings for each circuit breaker shall be as indicated on the drawings or data tables. Circuit breakers shall be 600-volt class.

        - Operating Mechanism: Mechanically and electrically trip-free, stored-energy operating mechanism with the following features:

          - Normal Closing Speed: independent of both control and operator

          - [Electrical operator, field installable with manual charging]

          - [Operations counter]

        - Each low voltage circuit breaker shall be equipped with self-powered, microprocessor-based trip-device to sense overload and short circuit conditions.  The device shall measure true RMS current.  The tripping system shall consist of high accuracy (<1%) Rogowski coil sensors on each phase, a release mechanism and the following features:

          - Field Installable and interchangeable front mounted trip units. Trip units can be upgraded for future expansion in functionality, such as communication.

          - Functions: Long time, short time and extended instantaneous protection function shall be provided (EIP) to allow the breaker to be applied at the withstand rating of the breaker with minus 0% tolerance so that there is no instantaneous override whatsoever. This feature shall furthermore allow the circuit breaker to be applied up to the full instantaneous rating of the breaker on systems where the available fault current exceeds the breakers withstand rating. Each shall have an adjustable pick-up setting.  In addition, long time and short time bands shall each have adjustable time delay.  Short time function shall include a switchable I2t ramp and optionally I4t to improve coordination with fuses or inverse relays.

          - A software program shall be made available free of charge to support system coordination studies.  The software will allow time current curves to be generated for the chosen settings.

          - Individual LED’s shall indicate an overcurrent, short circuit or ground fault trip condition.

          - Time-current characteristics shall be field adjustable locally or optionally remotely via a bus system [ModBus] [Profibus] [Ethernet].

          - Current Adjustability shall be accomplished by use of [dial settings] [keypad] and rating plugs on trip units.  The rating plug shall be front mounted and upgradeable.  Upgrades to the rating plugs shall not require changes to the CT.

          - Pickup Points: 10 Long Time Settings.

          - [Field Installable Ground-fault protection with at least three time-delay bands and an adjustable current pickup and an I2t ramp.]  Arrange to provide protection for [three-wire] [four-wire] service.

          - [Field installable zone selective interlocking: Connections will be made between main, tie and feeder circuit breakers to ensure that the circuit breaker closest to the fault trips for short time and ground fault conditions.]

          - [Field Installable Communications and metering functions shall be provided per schedule]

          - [A LCD display shall be available to simplify settings & viewing data locally.]

          - The option to remotely switch protection settings shall be provided whenever a generator is part of the power distribution system.

          - Field installable configurable [analog], [digital] output relays shall be available to connect directly to the trip unit

          - [Waveform capture and display shall be accomplished on the trip units LCD display. ETU776 only]

          - A visible pin shall indicate wear.  [In addition to the visible pin indicator, estimated contact wear shall be calculated in the trip unit and be [capable of being] communicated remotely.]

        - [Include a MOC (Mechanism Operated Cell switch) operated by the circuit breaker operating mechanism]

        - Terminal Block Connections, shall be front mounted and utilize [Screw Type Terminals], [Ring Tongue Terminals], [Tension Spring Terminals]

        - Padlocking Provisions shall be included to install at least three padlocks on each circuit breaker to prevent movement of the drawout mechanism.

        - Operating Handle shall be an integral part of the breaker.  No external tools shall be required to rack the breaker

        - [Control Switch: One for each electrically operated circuit breaker.]

        - [Key Interlocks: Mountings and hardware are included where future installation of key-interlock devices is indicated.]  A total of 14 different interlocking devices shall be available.

        - [Undervoltage Trip – field installable]: [Instantaneous] [Adjustable time-delay.]

        - [Shunt-Trip – field installable]

        - [Indicating Lights: To indicate circuit breaker is open or closed, for electrically operated circuit breakers.]

        - [Modular communication and relaying accessories are to be available for retrofitting by the clients chosen engineer.  It shall not be necessary for the manufacturer’s personnel to retrofit accessories.  ]

        - Accessories shall be front mounted.  Modular communications and relaying accessories are to be available for retrofitting by the clients chosen engineer.  It shall not be necessary for the manufacturer’s personnel to retrofit accessories.

        - Portable lifting yoke for drawout circuit breakers.

        - Field interchangeable accessories shall include CT’s, trip units, racking mechanism and all internal & external accessories.

        - [The main breaker shall have a Dynamic Arc Flash Sentry.  The main breaker shall have a dual protective setting capability with graphic waveform display, similar to the Siemens WL breakers ETU776 trip unit.  The main breaker will allow the installer to set two different trip curves into one breaker.  One curve will be set for standard operating mode and the second curve, with instantaneous protection shall be set for arc flash mode.   The switchboard shall be outfitted with a 24 VDC power supply, CubicleBus digital input module, annunciator panel with flashing light and a UPS power supply.  The arc flash mode shall be actuated by a [Siguard motion sensor set to the arc flash boundary] [keyed switch].  [A light curtain shall be installed behind the gear to sense open doors on the back of the panel.]]

    - Distribution Sections [NOTE: Select the type of section from below.]

      - [Panel-Mounted, Front Accessible

        - Individual sections shall be front accessible, not less than 20” deep and the rear of all sections shall align.  Incoming line termination, main device connection and all bolts used to join current-carrying parts shall be installed so as to permit servicing from the front only so that no rear access is required.  The branch devices shall be front removable and panel mounted with line and load side connections front accessible.  The interior shall be capable of accepting panel mounted molded case circuit breakers or fusible switches up to 1200 A rating.  Construction shall be Siemens SB type, or approved equal.]

      - [Individually Mounted, Rear Accessible (Insulated Case Breakers)

        - All sections shall be aligned front and rear.  Insulated case breakers shall be individually mounted in their own compartments.  Barriers shall be provided at the sides and rear of each compartment and a horizontal barrier between breakers in the same vertical section.  Breaker shall be accessible through a hinged metal door on each breaker compartment.  The insulated case circuit breaker shall be equal to Siemens WL Type and shall be self-contained to permit quick replacement, maintenance or inspection of breakers without de-energizing the entire switchboard. Construction shall be Siemens RCIII type, or approved equal.]

          - [Barriers shall be provided between the bus and cable compartment and between vertical sections.]

          - [Feeder device load terminal bus extensions shall be insulated.]

          - [Provide traveling type breaker lifting hoist and track mounted on top of switchboard.]

          - [Provide portable lifting device.]

    - Distribution Section Branch Protective Devices  [NOTE: Select the devices which apply to the switchboard  All molded case circuit breakers, fusible switches, Insulated case circuit breakers, bolted pressure switches, or low voltage power circuit breakers used as a protective device in a branch circuit shall meet the requirements of the appropriate paragraph below.]

      - [Molded Case Circuit Breakers

        - [Molded case circuit breakers shall be of quick-make, quick-break, trip-free.  The feeders shall be  [thermal magnetic] [solid-state – 150 amp frame, 30 amp trip and above]]

      - [Fusible Switches

        - Fusible switch: Fusible switch shall be of the quick-make, quick-break, trip-free type.  Switch shall be Siemens Vacu-break design or equivalent.  Switch ratings and options shall be shown on the drawings.

        - High contact pressure switch: High contact pressure switch shall be quick-make, quick-break, trip-free type.  Switch shall be Siemens HCP type or equivalent.  Switch ratings and options shall be shown on the drawings.]

      - [Bolted Pressure Switches

        - Each bolted pressure switch shall be the quick-make, quick-break type, equipped with Class L fuses suitable for application on a system with available fault current as shown on the drawings.  Ampere rating is to be as shown on the drawings.]

      - [Insulated Case Circuit Breakers

        - Each insulated case circuit breaker shall be [drawout] [stationary] frame, stored energy type, trip free, [manually operated] [electrically operated] with solid-state trip device.  Frame sizes and trip ratings to be as shown on the drawings.  All breakers shall have an interrupting capacity as indicated on the drawings.  Breakers shall be Siemens Type WL design or equivalent.]

    - [Multi-Metering Distribution Sections

      - Meter sockets shall be rated [100 amp] [200 amp] [320 amp] continuous duty.

      - Meter sockets shall contain [test blocks] [lever type manual bypass].

      - Meter cover design shall be [ring type] [ringless type].

      - Metering shall be [hot sequence] [cold sequence].

      - Load cables shall exit [top] [bottom].

      - Multi-metering branch protective devices shall be [molded case circuit breakers] [fusible switches] [fusible pullouts for Class T fuses].  ]

      - Each meter and associated disconnect device shall be labeled to easily identify meter/disconnect combinations.

      - All meter sockets (including provisions) shall be pre-wired.

    - Ground Fault Protection

      - Furnish and install in the service equipment and/or switchboard ground fault protection and indication equipment as specified herein and as shown on drawings in accordance with NEC 230-95.  All parts of the systems specified shall be UL Listed.  All new ground fault protection and indication equipment shall be factory installed, wired and tested by the switchboard manufacturer.

    - Metering Equipment

      - Provide a multi-function, high accuracy digital power metering instrumentation module equipped with LCD display.  The power metering module shall provide simultaneous measurements for current, voltage and power parameters.  Power meter shall be Siemens type [PAC 3100] [PAC 3200] [PAC4200] [9410] [9510] [9510 ADR/RTU] [9610] equipped with a communications port for standard RS-485 connection.

    - Finish

      - The complete switchboard shall be phosphatized and finished with ANSI 61 light gray polyester powder paint.

    - Markings

      - Each switchboard section shall have a label permanently affixed to it, listing the following information: Name of manufacturer, system voltage, ampacity, type, manufacturer's shop order number and date.

      - Each section of switchboard shall bear a UL listing mark, where qualified and a short circuit rating label.

      - Front, side, rear and top of each switchboard section will have a DANGER label in accordance with NEMA Standard PB-2.

    - [Optional Items]

      - [Provide Surge Protection Device for Low Voltage Circuits per specification Section [26 43 13.xx] [16289].

      - [Provide Electrical Power Monitoring and Control per specification Section [26 09 13.xx] [16290].

      - [Provide hinged wireway covers for front connected distribution sections.]

      - [Provide lighting panelboard interiors integral to the switchboard as shown on the drawings.]

      - [Provide key interlocks as indicated on associated electrical drawings.]

      - [All control wire shall be type SIS.]

      - NOTE: If this specification is for a NEMA 1 switchboard, then the space heater, humidistat and thermostat are all options.  If this specification is for a NEMA 3R switchboard, then a space heater is included as standard.  The thermostat or humidistat is optional.  [Space heaters and a [thermostat] [humidistat] shall be included in the switchboard.   Space heater shall be sized to prevent condensation.  The 120- volt power shall be derived from [a factory supplied CPT of the appropriate size for the space heater] [a customer supplied source].

    - [ARC FLASH [DELETE ONE OR BOTH OF THE FOLLOWING SENTENCES ON ARC FLASH]

      - [Apply in the field, the factory supplied arc flash warning label to all switchboards that are in other than dwelling occupancies and are likely to require examination, adjustment, servicing, or maintenance while energized to warn qualified persons of potential electrical arc flash hazards.]

      - [Provide a complete arc flash study of the entire electrical system from the point of incoming service to all panelboards.  Labels shall include the arc flash boundary in feet, hazard category and a list of appropriate PPE.]]

    - [Remote Racking

      - A remote racking device shall be supplied to allow qualified personnel to rack Siemens Type WL breakers into Connect, Test and Disconnect positions from up to 30 feet away from the breaker and outside the arc flash hazard boundary.

      - The remote racking device shall support utilization on any Frame Size 2 or Frame Size 3 WL breaker (including fuse carriage on fused Frame Size 3 WL breaker).

      - The remote racking device shall be portable and weigh less than 30 pounds (excluding cables and remote control panel).

      - The remote racking device shall have integral torque overload sensing to prevent damage to the breaker racking mechanism.

      - The remote racking device shall allow breaker to be racked to any position (disconnect, test, connect) regardless of the starting position of the breaker and without the need for user input as to the starting position.

      - The remote racking device shall support field retrofit on Type WL Low Voltage Switchboard.]

- EXECUTION

  - INSTALLATION

    - Examine substrates and conditions in which units will be installed.  Check for clearance that will be required before, during and after equipment installation.  Do not proceed with installation until unsatisfactory conditions are corrected.

    - Strictly comply with manufacturer's instructions and recommendations and NEMA PB 2.1.  Coordinate installation with adjacent work to ensure proper sequence of construction, clearances and support.

    - Install units plumb, level and rigid without distortion to the switchboard cubicle(s).

  - ADJUSTING AND CLEANING

    - Clean exposed surfaces using manufacturer recommended materials and methods.

    - Touch-up damaged coatings and finishes using non-abrasive materials and methods recommended by manufacturer.  Eliminate all visible evidence of repair.

  - TESTING

    - Perform factory and installation tests in accordance with applicable NEC, NEMA and UL requirements.

  - WARRANTY

    - Equipment manufacturer warrants that all goods supplied are free of non-conformities in workmanship and materials for one year from date of initial operation, up to eighteen months from date of shipment.

# END OF SECTION