# SECTION 26 33 43

ELECTRIC VEHICLE SUPPLY EQUIPMENT – DC HIGH POWER 150kW

PLUG-IN eBUS / FLEET CHARGING

- GENERAL

  - SCOPE

    - The requirements of the Contract, Division 26, applies to work in this section.  High Power Electric vehicle supply equipment (HP-EVSE) for DC Vehicle Charging as Specified and as shown on the contract drawings shall be furnished and installed by the Contractor.

  - RELATED DOCUMENTS

    - [Related Sections include the following:

      - [Section 26 28 16 – Substations]

      - [Section 26 13 13 – Medium Voltage Switchgear]

      - [Section 26 23 00 – Low Voltage Switchgear]

      - [Section 26 24 13 – Switchboards]]

  - SUBMITTALS

    - For review:

      - The following information shall be submitted to the Engineer:

        - Product data sheets

        - Installation manuals

    - For construction:

      - The following information shall be submitted for record purposes:

        - Final as-built overview drawings

        - Wiring diagrams

        - General layout floor plans

    - Installation information including equipment anchorage provisions.  The manufacturer shall provide final, as- built drawings, recording the general location of the supplied equipment, Installation layout, Operation and Maintenance manuals shall be supplied.

  - RELATED STANDARDS

    - The DC high-power electric vehicle supply equipment (HP-EVSE) shall be designed, manufactured and tested in accordance with the latest version of the following standards (unless otherwise noted):

      - SAE J1772, Electric Vehicle Conductive Charge Coupler

      - SAE J2894: Power Quality Requirements for Plug-In Electric Vehicle Chargers

      - Charging standard: EN61851-1/23/24

      - Communications: CCS using DIN 70121 and ISO 15118.

      - Safety: EN60950, IEC 950, UL1950

      - EV General Requirements: IEC 61851-1

      - DC Electric Charging station: IEC 61851-23

      - Vehicle connectors and inlets: IEC 62196-3

      - EN/IEC 61000-6-1 to EN/IEC 61000-6-4

      - Charging mode: Mode 4

      - Charging Connector: CCS type 1

      - UL 2202

      - UL 508C

      - Open Charge Point Protocol (OCPP) v1.6

  - QUALITY ASSURANCE

    - The manufacturer shall have been manufacturing HP-EVSE DC chargers or similar transportation electrification equipment for a minimum of three years.  The manufacture shall also have been in manufacturing for a minimum of ten years.

    - The HP-EVSE DC supplier shall manufacture “Make Ready” electrical infrastructure equipment to power and protect the charging equipment and provide an integrated HP-EVSE solution.

  - DELIVERY, STORAGE AND HANDLING

    - HP-EVSE DC provider shall build the DC high power chargers in the United States to conform to the Buy America Act requirement.

    - The HP-EVSE manufacture shall stock the DC high power components in the United States to facilitate fast and easy deliveries to the job site.

    - If HP-EVSE is being stored prior to installation, the HP-EVSE shall be stored to maintain the equipment in a clean and dry condition as required by the manufacturer’s instructions, in accordance with manufacturer’s instructions (1) copy of these instructions shall be included with the equipment at time of shipment.

- PRODUCTS

  - MANUFACTURERS

    - [The DC High Power Electric Vehicle Supply Equipment shall be Siemens eMobility or pre-approved equal.  Approved manufacturers are as follows:

      - SIEMENS eMobility – RAVE 150 Product Line

      - .]

    - Manufacturers listed above shall meet these specifications in their entirety. Products in compliance with the specification and manufactured by others not named shall be considered only if pre-approved by the Engineer ten (10) days prior to bid date.

    - Manufacture shall be able to provide a 150kW high power charger with output voltage ranges of 500 to 800Vdc.

    - Manufacture shall have the option for up to four (4) remote dispenser units tied to one Power Control cabinet.

    - The DC High Power charger shall be built in the U.S. to meet Federal Transit Authority (FTA) Buy America regulations.

  - PERFORMANCE REQUIREMENTS

    - 150kW power with 500 to 800Vdc range

    - Input Power: 3 phase, 480V AC Supply (+/-10%), 3 wires + PE Ground

    - Frequency: 57-63Hz

    - Input Current: 220A Maximum

    - Output Current: 200A

    - Output voltage ripple < 1%

    - Harmonics: <5% at full power, according to IEEE519

    - Efficiency: 95%

    - Power Factor: >0.98

    - Short Circuit Current Rating: 65kA @ 480VAC

    - Noise Level: 55dB

    - Operating Temperature: -13deg F to 122deg F (-25deg C to 50deg C)

    - Humidity:  95% relative humidity, non-condensing

    - Corrosion Resistance:  The enclosure coating shall have a corrosion resistance

    - Grounding System: PE grounded AC input / isolated DC output

    - Multiple HP-EV Dispensers:

      - System shall allow up to four Remote EV vehicle dispensers

      - Power control / power module unit shall have the ability to limit the power that can be delivered to the dispensers by means of a built-in control system or through remote software.

      - The system shall be capable of sequentially charging up to four vehicles from a single power cabinet

      - The system design shall support mounting of each remote dispenser up to 200 meters radially from the main power cabinet.

  - CONSTRUCTION

    - Provide a national recognized DC High Power charging station; quantities and current ratings as shown on the drawings.

    - Power / Control Cabinet Physical Specifications

      - The DC High Power charger shall be design as:

        - Power cabinet with remote charging dispenser(s)

      - Power Cabinet Construction and Finish

        - Enclosure shall be rated for outdoor, IP54/NEMA 3R to withstand severe weather requirements.

        - The cabinet size shall be approximately 58.2” x 33.8” x 87.2” (1479mm x 859mm x 2217mm) (WxDxH)

        - Cabinet installed weight: 5,291pounds (2400 kg)

        - Power cabinet shall have an incoming circuit breaker with lockable operating mechanism.

        - Enclosure shall have provisions for locking of unit.

        - An Emergency shut off button shall be integrated into the Power cabinet.

        - The Power cabinet shall have at least three levels of protection for current:

          - Software: Integrated PLC to continuously monitor the output current

          - Hardware: through a main circuit breaker or independent system, that will monitor data to drive current to zero if an overcurrent is detected.

          - Fuses: embedded fast acting fuses

        - Integrated Isolation Monitoring to stop charging if defined current threshold is exceeded.

        - Built in isolation transformer.

        - An Input EMC filter shall be provided to reduce the transfer of electromagnetic noise.

        - A rectifier bridge shall be incorporated into the cabinet to convert AC to DC current.

        - External and internal Identification label shall be provided with key current/voltage and model number information.

        - Surge arrester over voltage protection shall include:

            - Gas discharger component to protect against excess voltages on the neutral

            - A fast-acting voltage-dependent resistor

            - A set of varistors to protect the main and auxiliary transformers

        - A fully automated programmable logic control (PLC) system shall be incorporated to control the power and functionality of the system.

        - A Cooling fan with integrated filters shall be provided to ensure proper air quality.

      - Communications

        - The Power cabinet shall have two “built-in” options for hardwired communications to the remote dispenser:

          - Copper Ethernet, CAT6 or better with RJ45 connector within 328ft (100m)

          - Fiber Optic – Single mode 9um within 656ft (200m)

        - Integrated cellular communications shall be provided.

        - Cellular communications shall be 3G / 4G compatible with SIM card supplied.

        - A secure VPN router / solid state IoT unit shall be provided to collect, process and transfer data internally and to the vehicle during the charging session.

        - IoT unit will also provide Cloud connectivity for remote monitoring and control.

        - Communications shall be fully compatible with OCPP v1.6 (JSON) open protocol for backend systems. OCPP v2.0 ready.

        - Communications to the eVehicle shall be CCS using DIN 70121 and ISO 15118.

        - No access of live parts shall be required to update the communication elements of the charging station.

      - Data Collection and Monitoring

        - The manufacture shall provide a web-based dashboard for monitoring and control that will provide:

          - Charger Identification

          - Input voltage

          - DC output – voltage, current, power, energy delivered

          - Internal temperature readings

          - Date / time stamping of data

          - Realtime trending

          - Graphic screen of charging location with charging status indications

          - Alarming

          - SOC – State of Charge percentage

          - Vehicle ID and CP state

          - Vehicle target values: current, voltage, max. current & voltage

          - Vehicle battery capacity

          - Custom log files with at least the last 100 charging sessions

        - The manufacture shall offer a “Cloud” based solution to provide a customer with hosted data and monitoring from a web-based device.

        - Data shall be exportable to other software packages in XLS [Excel] or CSV [comma separated variable] formats

      - Remote Monitoring and Diagnostics

        - Remote diagnostics shall be provided via cellular connection.

        - Visibility to all aspects of the charger shall be available to enable remote troubleshooting by the manufacturer.

        - EVSE shall be capable of remote update of charging firmware / software.

        - Manufacturer shall offer remote 24x7 technical support.

      - Mounting

        - Enclosure shall come with detailed descriptions for installing the cabinet.

        - Complete wiring diagrams shall be provided to show wire type, size and terminations points.

        - Locations for entry / exit of wiring shall be shown.

        - Manufacture shall provide minimum space clearances for the cabinet to ensure accurate operations. Installer will need to reference local codes to ensure material in installed per regulations.

    - Remote Dispenser Charging Unit Physical Specifications

      - Remote dispenser shall be available in two designs:

        - Wall mount

        - Pedestal Mount

      - Remote dispenser charging cable shall have a CCS Type 1 connector with the following characteristics:

        - DC 2 x 2AWG

        - PE 1 x 6AWG

        - CP & CS 2x 16AWG

        - Temperature sensor 2 x 16AWG

      - Charging Cable Length shall be 25ft with CCS1 plug

      - Cable management system shall be provided with the remote dispenser.

      - An emergency stop button will be provided on the remote dispenser.

      - Standard CCS communications module will be used for powerline communications between the charger and vehicle.

      - Dispenser will incorporate DC output fuses to protect the charging station and vehicle from overcurrent.

      - Integrated Ethernet communications port for connection to the main Power / Control cabinet.

      - Communications between remote dispenser and power / control cabinet:

        - Copper Ethernet CAT6 up to 100m

        - Fiber Optic for distances for up to 200m

      - Dispenser HMI User Interface shall include:

        - A Color HMI touch screen display for monitoring and controlling the DCHP charger.

        - The HMI shall have at least the following languages available:

          - English

          - German

          - French

        - The HMI screens shall include at least the following information:

          - Status Bar to show status of the charging

            - Not Charging

            - Vehicle connected

            - Vehicle Charging

            - Charging complete

          - State of charging procedure

          - Charging power and supplied power

          - Charging voltage and current

          - Current state of charge in percent

          - Emergency Stop button

          - Secure locking state showing plug connector unlocked or locked

          - Alarms

            - Alarm history

            - Active Alarms

            - Alarm acknowledge button to allow clearing of alarms

            - Transformer High Temp alarm

            - Ground Fault Detection alarm

            - Cabinet Door is Open alarm

          - Charger Info

            - Working hours

            - Ventilation and cooling fan information

          - Energy Meter information for consumption and supplied energy

          - Graphic display of the charging cycle

          - Advanced Options screen for setup and configuration

          - Vehicle Shutdown LED displaying the reason for shutdown:

            - Charge Complete

            - System Incompatible

            - Voltage out of range

            - Current differential

            - Battery fault

            - Connector fault

            - Battery temperature

            - EV shift position

            - Unknown error

          - Graphic Trend screens for:

            - Power delivered

            - Total energy supplied by the charger

            - Input voltage by phase

            - DC output of Voltage and Current by the charger

- EXECUTION

  - INSTALLATION

    - All installation work shall be performed by a qualified person who is familiar with the installation, construction and operation of the equipment and the hazards involved.

    - Install per manufacturer’s recommendations and contract documents.

    - Install units’ plumb, level and rigid without distortion.

    - Installation of the DC Power Cabinet, Dispenser and Network connections shall follow the procedure in the published literature.

    - The Contractor shall install all equipment per the manufacturer’s recommendations and contract drawings.

    - All necessary hardware to secure the assembly in place shall be provided by the Contractor.

  - ADJUSTMENTS AND CLEANING

    - Remove debris from the Electric Vehicle Supply Equipment and wipe dust and dirt from all components.

    - Repaint marred and scratched surfaces with touch up paint to match original finish.

  - TESTING

    - Check tightness of all accessible mechanical and electrical connections to assure they are torqued to the minimum acceptable manufacture’s recommendations.

    - Check all installed charging systems for proper grounding, fastening and alignment.

    - Each EVSE shall undergo factory testing of all operational and protective features prior to shipment. No Onsight testing shall be required.

  - WARRANTY

    - Equipment manufacturer warrants that all goods supplied are free of non-conformities in workmanship and materials for two (2) years from date of shipment.

    - Changes or modifications to this product not authorized by the manufacturer shall void the warranty.  The contractor shall contact the manufacturer in order to avoid non-compliant modifications.

  - OPERATIONS AND MAINTENANCE MANUALS

    - Equipment operation and maintenance manuals shall be provided with each assembly shipped and shall include instruction leaflets and instruction bulletins for the complete assembly.

  - SERVICE

- DC EVSE Manufacture shall offer a managed service offering if required by end user.

- 24x7 Level 1 technical support line via a 1-800 number shall be provided.

- On-site startup assistance by the Manufacture shall be included

END OF SECTION