# SECTION 26 33 43

ELECTRIC VEHICLE SUPPLY EQUIPMENT – LEVEL 3 50kW DC FAST CHARGER

- GENERAL

  - SCOPE

    - The requirements of the Contract, Division 26, applies to work in this section for a 50kW DC Fast Charger electric vehicle solution, as Specified and as shown on the contract drawings which shall be furnished and installed by the Contractor.

  - RELATED DOCUMENTS

    - [Related Sections include the following:

      - [Section 26 28 16 – Substations]

      - [Section 26 13 13 – Medium Voltage Switchgear]

      - [Section 26 23 00 – Low Voltage Switchgear]

      - [Section 26 24 13 – Switchboards]]

  - SUBMITTALS

    - For review:

      - The following information shall be submitted to the Engineer:

        - Product data sheets

        - Installation manuals

    - For construction:

      - The following information shall be submitted for record purposes:

        - Final as-built overview drawings

        - Wiring diagrams

        - General layout floor plans

    - Installation information including equipment anchorage provisions.  The manufacturer shall provide final, as- built drawings, recording the general location of the supplied equipment, Installation layout, Operation and Maintenance manuals shall be supplied.

  - RELATED STANDARDS

    - The Level 3 DC Fast Charger electric vehicle supply equipment shall be designed, manufactured and tested in accordance with the latest version of the following standards (unless otherwise noted):

      - CHAdeMo, Electric Vehicle Conductive Charge Coupler

      - CCS, Type 1 or 2, Electric Vehicle Conductive Charge Coupler

      - OCPP 1.5 and 1.6J

      - CE, UL, RCM, IC

      - NEMA Type 3R

      - IP65 Rating

      - FCC Part 15.105

      - Security: SSH with EC keys & Unique password

      - National Electric Code, ANSI/NFPA 70

      - Charging standard: EN61851-1

      - Charging standard: EN61851-23

      - Communications: CCS using DIN 70121

      - Safety: EN60950, IEC 950, UL1950

      - EV General Requirements: IEC 61851-1

      - DC Electric Charging station: IEC 61851-23

      - Vehicle connectors and inlets: IEC 62196-3

      - EN/IEC 61000-6-1: FCC Part15, Subpart B (2014) & ICES-001 Issue 4 (2006)

      - EN/IEC 61000-6-2

      - EN/IEC 61000-6-3: FCC Part 15, Subpart B (2014) & ICES-001 Issue 4 (2006)

      - EN/IEC 61000-6-4, part EN55011 Class A, Group 1

      - Charging mode: Mode 4 (DCFC)

      - Charging Connector: CCS type 1

      - UL 2202

      - Open Charge Point Protocol (OCPP) v1.6

    - Products shall be listed or approved by Underwriters Laboratories, Inc.

  - QUALITY ASSURANCE

    - The manufacturer shall have been manufacturing 50kW DC Fast chargers or similar transportation electrification equipment for a minimum of three years.

    - The DC Fast Charger supplier shall manufacture “Make Ready” electrical infrastructure equipment to power and protect the charging equipment, providing an integrated EVSE solution.

  - DELIVERY, STORAGE AND HANDLING

    - DC Fast charger provider shall build the Level 3 50kW power chargers in the United States to conform to the Buy America Act requirement.

    - The DC Fast charger manufacture shall stock the units and power components in the United States to facilitate fast and easy deliveries to the job site.

    - If DC Fast charger is being stored prior to installation, the unit shall be stored to maintain the equipment in a clean and dry condition as required by the manufacturer’s instructions, in accordance with manufacturer’s instructions (1) copy of these instructions shall be included with the equipment at time of shipment.

- PRODUCTS

  - MANUFACTURERS

    - [The 50 kW DC Fast Charger Electric Vehicle Supply Equipment shall be provided by Siemens eMobility or pre-approved equal.  Approved manufacturers are as follows:

      - SIEMENS eMobility – 50kW DC Fast Charger Product Line

      - .]

    - Manufacturers listed above shall meet these specifications in their entirety. Products in compliance with the specification and manufactured by others not named shall be considered only if pre-approved by the Engineer ten (10) days prior to bid date.

    - The 50kW charger shall be built / assembled in the U.S. to meet Buy America compliant regulations.

  - PERFORMANCE REQUIREMENTS

    - 50kW power with 380 to 4800V ac range, 3 phase

    - Input Power needed:

      - 3 phase, WYE, 277/480V AC Supply (+/-10%), 3 wires, 55kW

      - 1 phase, 120V, 60Hz, 250W

    - Frequency: 57-63Hz

    - Input Current: 100A common

    - Output Current: 125A Max

    - Output voltage: 50V – 500V

    - Noise Level: 0 to 57dB with fan running

    - Temperature: -31deg F to 122deg F (-35deg C to 50deg C)

    - Humidity

      - 95% relative humidity, non-condensing

    - Corrosion Resistance

      - The enclosure coating or design shall have a corrosion resistance

    - Dual Charging Ports:

      - The unit shall allow up to two EV vehicle dispensers supporting two vehicles

    - Charging will be in series for the two ports by varying the charging stations power by means of a built-in control system or through remote software.

    - Integrated Power control / power module unit shall be used to provide one free-standing unit. No dual cabinet designs will be provided.

  - CONSTRUCTION

    - Provide a national recognized 50kW, free-standing, single unit design, DC Fast Charger; quantities and locations as shown on the drawings.

    - An Integrated DC Power and Control cabinet design shall be provided. No two-piece designs shall be permitted increasing the installation and wiring costs.

    - The DC Fast Charger shall come standard supporting two ports.

    - The dispenser types shall include at least CHAdeMo and CCS type 1 or 2.

    - The charger will support any mixture of dispensers.

      - Dual CHAdeMo style

      - Dual CC style

      - CHAdeMo and CCS

    - Enclosure shall be rated for outdoor, IP65 / NEMA 3R to withstand severe weather requirements.

    - The integrated fast charger cabinet size shall be:

      - 29.5” (W) x 78.7”(H) x 13” (D)  /  (750mm (W) x 2000mm (H) x 330mm (D)

    - Cabinet installed weight: 364 pounds (165 kg)

    - An Emergency shut off button shall be integrated into the front of the DC Fast Charger cabinet.

    - Unit shall include built in main transformer.

    - A rectifier bridge shall be incorporated into the cabinet to convert AC to DC current.

    - A Cooling fan shall be provided to ensure proper air quality.

    - Radiator fan shall be removable to assist in installation if needed.

    - Charging cable shall be at least 6.5ft long with integrated provision for plugging in cable when not in use.

    - Support for integrated hardwired Ethernet communications.

    - Power shall be provided either through a bottom or side conduit open to ensure ease of installation.

    - Integrated lifting straps shall be provided into the charger for ease of mounting.

    - Single phase 120v power cable shall be supplied to allow temporary setup and updates prior to installation.

  - INTERFACE PANEL

Integrated interface panel shall be provided to facilitate end-user ease of use. This interface will supply at least these icons and readings:

    - Connect / Ready to use light up icon

    - Max % toggle button to allow specific percentage to be chosen.

    - Start Button

    - Stop Button

    - Return plug to charger icon. Flashes when charging session is done.

    - Not in-Service lighted icon.

    - Locked symbol indicator lighted icon.

    - Charging indicator. Glows when the charging session is in progress.

    - LED informational display showing:

      - Minutes

      - Battery percentage during charge

      - Kilowatts delivered

      - Fee charged

  - PAYMENT INTERFACE

The DC Fast Charger shall incorporate integrated customer payment methods. Payment shall be provided by:

    - Integrated RFID swipe feature

    - APP or SMS activation

    - Optional standard credit card reader

  - COMMUNICATIONS

    - The DC Fast Charger shall have a “built-in” Gigabit Ethernet communications port.

      - Copper Ethernet, CAT6 or better with RJ45 connector

    - An integrated 3G/4G Cellular communications model shall be provided.

    - Communications shall be fully compatible with OCPP 1.5 and v1.6j (JSON) open protocol for backend systems.

    - Standard data communicated via OCPP will include:

      - Session ID

      - Vendor ID

      - EVSEID

      - Port ID

      - Number of ports on the EVSE

      - Charge Start date and time

      - Charge End date and time

      - Charge Duration – time power being provided to EV

      - Session (connection) start date and time – when port is connected to EV

      - Session (connection) send date and time – when port is disconnected to EV

      - Session Connection Time

      - Charge kWh usage - per session

      - Charge Max Demand kW – per session

      - Session Sale Amount – Fees charged to end user

      - Vehicle Make - optional

      - Vehicle Model – optional

      - User ID – Anonymous user ID – optional

    - No access of live parts shall be required to update the communication elements of the charging station.

  - CUSTOMER FACING DESIGN

    - The DC Fast Charger shall allow for “custom” front and rear decals to allow company logos, messages and names to be displayed.

    - Option for a large HMI display integrated into the DC Fast Charger unit.

  - DATA COLLECTING AND MONITORING

    - The manufacture shall offer a “Cloud” based solution to provide a customer with hosted data and monitoring from a web-based device.

    - Remote maintenance shall be provided by a web server (IP) connection.

    - Visibility to all aspects of the charger will be provided for troubleshooting, maintenance, updating charging software and support.

    - Remote 24x7 maintenance support shall be offered by the manufacture.

  - MOUNTING

    - Enclosure shall come with mounting plate and detailed descriptions for installing the cabinet.

    - Complete wiring diagrams shall be provided to show wire type, size and terminations points.

    - Locations for entry / exit of wiring shall be shown.

    - Manufacture shall provide minimum space clearances for the cabinet to ensure accurate operations. Installer will need to reference local codes to ensure material in installed per regulations.

    - Mounting shall be on a concrete foundation with supporting conduit hole, as recommended by the manufacture.

    - Power shall be provided either through a bottom or side conduit open to ensure ease of installation.

    - Integrated lifting straps shall be provided into the charger for ease of mounting.

- EXECUTION

  - INSTALLATION

    - All installation work shall be performed by a qualified person who is familiar with the installation, construction and operation of the equipment and the hazards involved.

    - Install per manufacturer’s recommendations and contract documents.

    - Install units’ plumb, level and rigid without distortion.

    - Installation of the 50kW Fast Charger shall follow the procedure in the published literature.

    - The Contractor shall install all equipment per the manufacturer’s recommendations and contract drawings.

    - All necessary hardware to secure the assembly in place shall be provided by the Contractor.

  - ADJUSTMENTS AND CLEANING

    - Remove debris from the Electric Vehicle Supply Equipment and wipe dust and dirt from all components.

    - Repaint marred and scratched surfaces with touch up paint to match original finish.

  - TESTING

    - Check tightness of all accessible mechanical and electrical connections to assure they are torqued to the minimum acceptable manufacture’s recommendations.

    - Check all installed charging systems for proper grounding, fastening and alignment.

    - Each EVSE shall undergo factory testing of all operational and protective features prior to shipment. No Onsight testing shall be required.

  - WARRANTY

    - Equipment manufacturer warrants that all goods supplied are free of non-conformities in workmanship and materials for three (3) years from date of shipment.

    - Changes or modifications to this product not authorized by the manufacturer shall void the warranty.  The contractor shall contact the manufacturer in order to avoid non-compliant modifications.

  - OPERATIONS AND MAINTENANCE MANUALS

    - Equipment operation and maintenance manuals shall be provided with each assembly shipped and shall include instruction leaflets and instruction bulletins for the complete assembly.

  - SERVICE

- DC Fast Charger supplier shall offer a managed service offering if required by end user.

- 24x7 Level 1 technical support line via a 1-800 number shall be provided at no cost.

- On-site startup assistance by the supplier shall be offered as part of the package.

END OF SECTION