SECTION 26 43 13

SURGE PROTECTIVE DEVICES (SPDs) - INTERNALLY MOUNTED

FOR LOW-VOLTAGE ELECTRICAL POWER CIRCUITS

- GENERAL

  - SCOPE

    - This section describes the materials and installation requirements for surge protective devices (SPD) for the protection of all AC electrical circuits.

  - RELATED DOCUMENTS

    - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

    - [Other sections that may relate to the work in this section include, but are not limited to, the following:

      - Section 26 24 13 – Switchboards

      - Section 26 24 16 – Panelboards

      - Section 26 24 19 – Motor Control Centers

      - Section 26 25 00 – Busway]

  - SUBMITTALS

    - Submit shop drawings and product information for approval and final documentation in the quantities listed according to the Conditions of the Contract. All transmittals shall be identified by customer name, customer location, and customer order number.

    - Submittals shall include UL 1449 4th Edition Listing documentation verifiable by visiting www.UL.com, clicking “Certifications” link, searching using UL Category Code: VZCA and VZCA2:

- Short Circuit Current Rating (SCCR)

- Voltage Protection Ratings (VPRs) for all modes

- Maximum Continuous Operating Voltage rating (MCOV)

- I-nominal rating (I-n)

- SPD shall be UL 1449 4th Edition as a Type 2 Component or Listed Assembly. When connected to supply or utility side of service SPD shall be labeled as Type 1.

    - Upon request, an unencapsulated, complete SPD formally known as TVSS shall be presented for visual inspection.

    - Minimum of ten (10) year warranty

  - RELATED STANDARDS

    - IEEE C62.41.1, IEEE Guide on the Surge Environment in Low-Voltage (1000 V and Less) AC Power Circuits,

    - IEEE C62.41.2, IEEE Recommended Practice on Characterization of Surges in Low-Voltage (1000 V and Less) AC Power Circuits,

#### IEEE C62.45, IEEE Recommended Practice on Surge Testing for Equipment Connected to Low-Voltage (1000 V and Less) AC Power Circuits.

#### National Electrical Code: Article 285, 620, 670, 695, 700, and 708

    - UL 1283 - Electromagnetic Interference Filters (Type 2 only)

    - UL 1449, 4th Edition, effective March 26, 2015 – Surge Protective Devices

  - QUALITY ASSURANCE

    - Manufacturer Qualifications:  Engage a firm with at least 5 years experience in manufacturing transient voltage surge suppressors.

    - Manufacturer shall be ISO 9001 or 9002 certified.

    - The manufacturer of this equipment shall have produced similar electrical equipment for a minimum period of ten (10) years. When requested by the Engineer, an acceptable list of installations with similar equipment shall be provided demonstrating compliance with this requirement.

    - The SPD shall be compliant with the Restriction of Hazardous Substances (RoHS) Directive 2002/95/EC.

  - DELIVERY, STORAGE AND HANDLING

    - Handle and store equipment in accordance with manufacturer’s Installation and Maintenance Manuals.  One (1) copy of this document to be provided with the equipment at time of shipment.

- PRODUCTS

  - MANUFACTURERS

    - Provide an internally mounted Surge Protective Devices (SPD) formally called Transient Voltage Suppressor (TVSS) by:

      - SIEMENS

      - [Pre-approved equal]

  - ELECTRICAL DISTRIBUTION EQUIPMENT

    - [[Service Entrance] [Emergency Power Switchboard] [Meter Centers]

SPD shall be factory installed integral to electrical distribution equipment, and it shall be UL 1449 labeled as Type 2, verifiable at UL.com, without need for external or supplemental overcurrent controls.  Every suppression component of every mode, including N-G, shall be protected by internal overcurrent and thermal overtemperature controls.  SPDs relying upon external or supplementary installed safety disconnectors do not meet the intent of this specification.

      - SPD shall be UL labeled with 20kA I-nominal (I-n) (verifiable at UL.com) as recommended for UL 96A Lightning Protection Master Labeling and NFPA 780.

SPD shall be UL labeled with 200kA Short Circuit Current Rating (SCCR).

      - SPD shall provide surge current paths for all modes of protection: L-N, L-G, L-L, and N-G for Wye systems; L-L, L-G in Delta and impedance grounded Wye systems.

      - SPD shall be connected to the buss of the distribution equipment with an appropriately sized 200kA SCCR rated disconnect.

      - SPD shall meet or exceed the following criteria:

        - Maximum surge current capability shall be 300kA per phase.

        - UL 1449 - Fourth Edition Revision; effective March 26, 2015 Voltage Protection Ratings shall not exceed the following:

| VOLTAGE | L-N | L-G | N-G | L-L | MCOV |
| --- | --- | --- | --- | --- | --- |
| 208Y/120 | 700V | 700V | 700V | 1200V | 150V |
| 480Y/277 | 1200V | 1200V | 1200V | 2000V | 320V |

      - UL 1449 Listed Maximum Continuous Operating Voltage (MCOV) (verifiable at UL.com):

| System Voltage |  | Allowable System Voltage Fluctuation (%) |  | MCOV |
| --- | --- | --- | --- | --- |
| 208Y/120 |  | 25% |  | 150V |
| 480Y/277 |  | 15% |  | 320V |

      - SPD shall incorporate a UL 1283 listed EMI/RFI filter with minimum attenuation of - 50dB at 100 kHz.

      - Suppression components shall be heavy duty ‘large block’ MOVs, each exceeding 30mm diameter.

      - SPD shall include a serviceable, replaceable module.

      - SPD shall be equipped with the following diagnostics:

        - Visual LED diagnostics including a minimum of one green LED indicator per phase, and one red service LED.

        - Audible alarm with on/off silence function and diagnostic test function (excluding branch).

        - Form C dry contacts

        - Surge Counter

No other test equipment shall be required for SPD monitoring or testing before or after installation.

      - SPD shall have a response time no greater than 1/2 nanosecond.

      - SPD shall have a 10 year warranty.]

    - [[Distribution Panel] [Emergency Power Panels] [Motor Control Center] [Busway]

      - SPD shall be factory installed integral to electrical distribution equipment, and it shall be UL 1449 labeled as Type 2, verifiable at UL.com, without need for external or supplemental overcurrent controls.  Every suppression component of every mode, including N-G, shall be protected by internal overcurrent and thermal overtemperature controls.  SPDs relying upon external or supplementary installed safety disconnectors do not meet the intent of this specification.

      - SPD shall be factory installed integral to electrical distribution equipment.

      - SPD shall be UL labeled with 20kA I-nominal (I-n)

      - SPD shall be UL labeled with 200kA Short Circuit Current Rating (SCCR).

      - SPD shall provide surge current paths for all modes of protection: L-N, L-G, L-L, and N-G for Wye systems; L-L, L-G in Delta and impedance grounded Wye systems.

      - SPD shall be connected to the buss of the distribution equipment with an appropriately sized 200kA SCCR rated disconnect.

      - SPD shall meet or exceed the following criteria:

        - Maximum surge current capability shall be 150kA per phase.

        - UL 1449 - Fourth Edition Revision; effective March 26, 2015 Voltage Protection Ratings shall not exceed the following:

| VOLTAGE | L-N | L-G | N-G | L-L | MCOV |
| --- | --- | --- | --- | --- | --- |
| 208Y/120 | 700V | 700V | 700V | 1200V | 150V |
| 480Y/277 | 1200V | 1200V | 1200V | 2000V | 320V |

      - UL 1449 Listed Maximum Continuous Operating Voltage (MCOV) for L-N, L-G, and N-G modes of protection (verifiable at UL.com):

| System Voltage |  | Allowable System Voltage Fluctuation (%) |  | MCOV |
| --- | --- | --- | --- | --- |
| 208Y/120 |  | 25% |  | 150V |
| 480Y/277 |  | 15% |  | 320V |

      - SPD shall incorporate a UL 1283 listed EMI/RFI filter with minimum attenuation of - 50dB at 100 kHz.

      - Suppression components shall be heavy duty ‘large block’ MOVs, each exceeding 30mm diameter.

      - SPD shall include a serviceable, replaceable module.

      - SPD shall be equipped with the following diagnostics:

        - Visual LED diagnostics including a minimum of one green LED indicator per phase, and one red service LED.

        - Audible alarm with on/off silence function and diagnostic test function (excluding branch).

        - Form C dry contacts

        - Surge Counter

No other test equipment shall be required for SPD monitoring or testing before or after installation.

      - SPD shall have a response time no greater than 1/2 nanosecond.

      - SPD shall have a 10 year warranty.]

    - [[Branch Panels] [Emergency Branch Panels]

      - The panelboard shall be UL 67 Listed and the SPD shall be UL 1449 Type 2 applications.

      - The unit shall be top or bottom feed according to requirements. A circuit directory shall be located inside the door.

      - SPD shall be factory installed integral to electrical distribution equipment, and it shall be UL 1449 labeled as Type 2, verifiable at UL.com, without need for external or supplemental overcurrent controls.  Every suppression component of every mode, including N-G, shall be protected by internal overcurrent and thermal overtemperature controls.  SPDs relying upon external or supplementary installed safety disconnectors do not meet the intent of this specification.

      - SPD shall be factory installed integral to electrical distribution equipment.

      - SPD shall be UL labeled with 20kA I-nominal (I-n)

      - SPD shall be UL labeled with 200kA Short Circuit Current Rating (SCCR).

      - SPD shall provide surge current paths for all modes of protection: L-N, L-G, L-L, and N-G for Wye systems; L-L, L-G in Delta and impedance grounded Wye systems.

      - SPD shall be connected to the buss of the distribution equipment with an appropriately sized 200kA SCCR rated disconnect.

      - SPD shall meet or exceed the following criteria:

        - Maximum surge current capability shall be 100kA per phase.

        - UL 1449 - Fourth Edition Revision; effective March 26, 2015 Voltage Protection Ratings shall not exceed the following:

| VOLTAGE | L-N | L-G | N-G | L-L | MCOV |
| --- | --- | --- | --- | --- | --- |
| 208Y/120 | 700V | 700V | 700V | 1200V | 150V |
| 480Y/277 | 1200V | 1200V | 1200V | 2000V | 320V |

      - UL 1449 Listed Maximum Continuous Operating Voltage (MCOV) (verifiable at UL.com):

| System Voltage |  | Allowable System Voltage Fluctuation (%) |  | MCOV |
| --- | --- | --- | --- | --- |
| 208Y/120 |  | 25% |  | 150V |
| 480Y/347 |  | 15% |  | 320V |

      - SPD shall incorporate a UL 1283 listed EMI/RFI filter with minimum attenuation of - 50dB at 100 kHz.

      - Suppression components shall be heavy duty ‘large block’ MOVs, each exceeding 30mm diameter.

      - SPD shall include a serviceable, replaceable module.

      - SPD shall be equipped with the following diagnostics:

        - Visual LED diagnostics including a minimum of one green LED indicator per phase, and one red service LED.

        - Audible alarm with on/off silence function and diagnostic test function

        - Form C dry contacts

        - Surge Counter

No other test equipment shall be required for SPD monitoring or testing before or after installation.

      - SPD shall have a response time no greater than 1/2 nanosecond.

      - SPD shall have a 10 year warranty.

      - The unit shall have removable interior.

      - The main bus shall be [copper] [aluminum] and rated for the load current required.

      - The unit shall include a 200% rated neutral assembly with copper neutral bus.

      - The unit shall be provided with a safety ground bus.

      - The field connections to the panelboard shall be main lug or main breaker.

      - The unit shall be constructed with flush or surface mounted trim and shall be in a NEMA Type 1 enclosure.]

- EXECUTION

  - INSTALLATION

    - Install per manufacturer’s recommendations and contract documents.

  - ADJUSTMENTS AND CLEANING

    - Remove debris from installation site and wipe dust and dirt from all components.

    - Repaint marred and scratched surfaces with touch up paint to match original finish.

  - TESTING

    - Check tightness of all accessible mechanical and electrical connections to assure they are torqued to the minimum acceptable manufacture’s recommendations.

    - Check all installed panels for proper grounding, fastening and alignment.

  - WARRANTY

    - Equipment manufacturer warrants that all goods supplied are free of non-conformities in workmanship and materials for one year from date of initial operation, but not more than eighteen months from date of shipment.

END OF SECTION