## Voltage Drop Calculator
Estimated Voltage Drop Calculator
Project Name
Firm Name
Date
Engineer
Feeder Data
Input
Load Voltage
Conductor Size
|  | Conductor Type |  | Cu | Al
Number of Sets
|  | Distance (one way) |  |  | Feet
|  | Load (A) |  |  | A
Output
|  | Unity Power Factor |  |  |  |  | 85% PF
|  | Voltage Drop (V) |  | 0 | V |  | 0 | V
|  | Voltage Drop (%) |  | 0 | % |  | 0 | %
|  | Voltage at Load |  | 120 | V |  | 120 | V
Minimum Conductor Size for 3% VD
Minimum Conductor Size for 5% VD
[11 empty] | Z in Steel Ohms per 1000 feet | [5 empty] | pf 1.0 |  | Tables Offset for Min Size
|  |  | V | Multiplier |  |  | Size | Cmil |  |  | CU 1.0 | CU .85 | AL 1.0 | AL .85 | R DC Cu | R DC Al | Q Cu | Q Al | Size | Cmil
| 1 | 120 V 1Ø | 120 | 2 |  | 1 | 14 | 4110 | 1 | 14 | 3.1 | 2.7 |  |  | 3.07 | 5.06 | 1 | 1 | 14 | 1
| 2 | 208V 1Ø | 208 | 2 |  | 2 | 12 | 6530 | 2 | 12 | 2 | 1.7 | 3.2 | 2.8 | 1.93 | 3.18 | 1 | 1 | 12 | 4110
| 3 | 208V 3Ø | 208 | 1.732 |  | 3 | 10 | 10380 | 3 | 10 | 1.2 | 1.1 | 2 | 1.8 | 1.21 | 2 | 1 | 1 | 10 | 6530
| 4 | 240V 1Ø | 240 | 2 |  | 4 | 8 | 16510 | 4 | 8 | 0.78 | 0.7 | 1.3 | 1.1 | 0.809 | 1.26 | 1 | 1 | 8 | 10380
| 5 | 240 3Ø | 240 | 1.732 |  | 5 | 6 | 26240 | 5 | 6 | 0.49 | 0.45 | 0.81 | 0.72 | 0.491 | 0.808 | 1 | 1 | 6 | 16510
| 6 | 277V 1Ø | 277 | 2 |  | 6 | 4 | 41740 | 6 | 4 | 0.31 | 0.3 | 0.51 | 0.46 | 0.308 | 0.508 | 1 | 1 | 4 | 26240
| 7 | 480V 1Ø | 480 | 2 |  | 7 | 3 | 52620 | 7 | 3 | 0.25 | 0.24 | 0.4 | 0.37 | 0.245 | 0.403 | 1 | 1 | 3 | 41740
| 8 | 480V 3Ø | 480 | 1.732 |  | 8 | 2 | 66360 | 8 | 2 | 0.2 | 0.2 | 0.32 | 0.3 | 0.194 | 0.319 | 1 | 1 | 2 | 52620
[6 empty] | 9 | 1 | 83690 | 9 | 1 | 0.16 | 0.16 | 0.25 | 0.25 | 0.154 | 0.253 | 1 | 1 | 1 | 66360
|  | K |  |  |  | 10 | 1/0 | 105600 | 10 | 1/0 | 0.12 | 0.13 | 0.2 | 0.2 | 0.122 | 0.201 | 1 | 0.99502 | 1/0 | 83690
|  | Cu | 12.9 |  |  | 11 | 2/0 | 133100 | 11 | 2/0 | 0.1 | 0.11 | 0.16 | 0.16 | 0.0967 | 0.159 | 1.0341 | 1.0063 | 2/0 | 105600
|  | Al | 21.2 |  |  | 12 | 3/0 | 167800 | 12 | 3/0 | 0.079 | 0.094 | 0.13 | 0.14 | 0.0766 | 0.126 | 1.0313 | 1.0317 | 3/0 | 133100
[6 empty] | 13 | 4/0 | 211600 | 13 | 4/0 | 0.063 | 0.08 | 0.1 | 0.11 | 0.0608 | 0.1 | 1.0362 | 1 | 4/0 | 167800
|  | Interim Calculations |  |  |  | 14 | 250 | 250000 | 14 | 250 | 0.054 | 0.073 | 0.086 | 0.1 | 0.0515 | 0.0847 | 1.0485 | 1.0153 | 250 | 211600
|  | Conductor |  | 2 |  | 15 | 300 | 300000 | 15 | 300 | 0.045 | 0.065 | 0.072 | 0.088 | 0.0429 | 0.0707 | 1.049 | 1.0184 | 300 | 250000
|  | CM |  | 6530 |  | 16 | 350 | 350000 | 16 | 350 | 0.039 | 0.06 | 0.063 | 0.08 | 0.0367 | 0.0605 | 1.0627 | 1.0413 | 350 | 300000
|  | Sets |  | 1 |  | 17 | 400 | 400000 | 17 | 400 | 0.035 | 0.056 | 0.055 | 0.073 | 0.0321 | 0.0529 | 1.0903 | 1.0397 | 400 | 350000
|  | Q |  | 1 |  | 18 | 500 | 500000 | 18 | 500 | 0.029 | 0.05 | 0.045 | 0.064 | 0.0258 | 0.0424 | 1.124 | 1.0613 | 500 | 400000
|  | System |  | 1 |  | 19 | 600 | 600000 | 19 | 600 | 0.025 | 0.047 | 0.038 | 0.058 | 0.0214 | 0.0353 | 1.1682 | 1.0765 | 600 | 500000
|  | Cu/Al |  | 1 |  | 20 | 750 | 750000 | 20 | 750 | 0.021 | 0.043 | 0.031 | 0.052 | 0.0171 | 0.0282 | 1.2281 | 1.0993 | 750 | 600000
|  | V |  | 120 |  | 21 | 1000 | 1000000 | 21 | 1000 | 0.018 | 0.04 | 0.025 | 0.046 | 0.0129 | 0.0212 | 1.3953 | 1.1792 | 1000 | 750000
|  | Multiplier |  | 2 | [14 empty] | 1100 | 1000000
|  | K |  | 12.9
|  | Min CM for 3% |  | 0
|  | Min CM for 5% |  | 0
|  | Size for 3% |  | #N/A
|  | Size for 5% |  | #N/A
|  | Zac per ft 1.0pf |  | 2
|  | Zac per ft .85pf |  | 1.7
vers. 9.2019

## Summary
Voltage Drop Summary
Project Name:
Engineer:
Date:
| Feeder Designation | Source Panel | Source Circuit | Vd (V) | Vd (%)
vers. 9.2019

## Information
Information
This voltage drop calculator is based on public domain formulae and will provide an approximate value for use in project design. The National Electrical Code™ Articles 210.19(A)(1) FPN No.4 and 215.2(A)(3) FPN No.2 suggest that a design with no more than 3% voltage drop for feeders and no more than a total of 5% voltage drop in branch circuits to the farthest outlet will "provide reasonable efficiency of operation".
Even though FPN's (fine print notes) in this case are not code requirements but recommendations, it is still good engineering practice to closely follow these guidelines, and indeed exceed them where needed. In fact, Section 647, Sensitive Electronic Equipment, requires (not an FPN) that voltage drop for feeders and branches shall not exceed 1.5% and 2.5%, respectively, and shall not exceed 1% and 2% respectively for cord-connected equipment. Fire pumps have additional maximum voltage drop requirements and these are outlined in Section 695.
If you do increase the size of your conductors to accommodate for voltage drop, remember to check if the new conductor size is compatible with the lugs to which they will be attached. The circuit breaker manufacturers make available the acceptable conductor sizes, and in some cases offer optional larger lugs for this purpose. Also, Article 250 requires that if the conductors are upsized, the grounding conductor must also be upsized proportionately.
The unity power factor section of this program is based on the approximate voltage drop formula Vd = (2 K Q I D) / CM for single phase and Vd = (1.732 K Q I D) / CM for three phase where K equals 12.9 for Copper and 21.2 for Aluminum, Q is the ratio of Rac/Rdc for conductors larger than 2/0 (this takes into account skin effect at larger conductor sizes), I is the current in amperes, D is the one-way circuit distance in feet, and CM is the conductor cross section in circular mils. This equation assumes a power factor of 1.0, conductor temperature of 75°C, and individual conductors run in steel conduit. The 85% power factor section is based on NEC™ Chapter 9, Tables 8 and 9.
Printing - When printing the Voltage Drop Calculator sheet, go to File/Print Preview and select "black & white" from the Print options.
vers. 9.2019